भारतीय मानक

विधुत मीटर रीडिंग, शुल्क और लोड नियंत्रण के लिए

आंकड़ों का विनिमय- सहयोगी विशिष्टि

भाग 1 स्थैतिक ऊर्जा मीटर

***Indian Standard***

**DATA EXCHANGE FOR ELECTRICITY METER**

**READING, TARIFF AND LOAD CONTROL —**

**COMPANION SPECIFICATION**

Part 1 Static Energy Meter

ICS 17.220.20;35.100.01;91.140.50

© BIS 2011

**B U R E A U O F I N D I A N S T A N D A R D S**

MANAK BHAVAN, 9 BAHADUR SHAH ZAFAR MARG

NEW DELHI 110002

*October* 2023 **Price Group 12**

Equipment for Electrical Energy Measurement, Tariff and Load Control Sectional Committee, ETD 13

FOREWORD

This Indian Standard was adopted by the Bureau of Indian Standards, after the draft finalized by the Equipment for Electrical Energy Measurement, Tariff and Load control Sectional Committee had been approved by the Electrotechnical Division Council.

With development of electronic meters having possibilities of metering data being integrated into business processes of service providers and in turn with generating agencies, thus opening up multiple opportunities in power system management at both micro and macro levels and being guided by the National Electricity Policy of the Central Government after enactment of the *Electricity Act,* 2003, the Committee initiated the work of formulating standards on Data Exchange for Electricity Metering Equipment in 2006.

Two options were taken up for interoperable use of meters in a data network. In 2007, the Committee decided to adopt the International Standard IEC 62056, already available in various parts. However, it was felt that only adoption was not sufficient for proper implementation as the selective features of the standard available at that time were not adequate for use by different utilities collectively. In view of urgent power reforms programme of the Central Government and the metering data integration involved, the Electrotechnical Division Council in April 2008, while appreciating the other option of Common Framework based solution being developed by [Indian Electrical and Electronics Manufacturers Association](http://www.ieema.org/) (IEEMA), advised the committee and divergent stakeholders for rapid implementation of the IEC standard available. The Committee inducted experts and held a series of meetings for evolving this Indian Standard for proper implementation of the IEC standard based on open protocol and wide-ranging selective features thereof, for application in Indian networks.

The Central Electricity Authority (CEA), a body under the *Electricity Act 2003*, to prepare regulations on installation and operation of meters and to record data regarding electricity from generation to utilization and the Central Power Research Institute, a Society under the Central Government, with established conformance test facilities for meters conforming to IEC62056 at its Bangalore Laboratory, both members of the Committee, were involved in preparation of category wise comprehensive list of metering parameters for use in national networks. The Report titled “Standardization of Metering Parameters” finalized with object identifier codes as requested was submitted to BIS in April 2009 for facilitating preparation of Indian Standards/Guides on Metering data exchange. Some assistance has also been derived from CBIP Publication 304 Manual on Standardization of AC Static Electrical Energy Meters (for electrical energy and tariff related parameter terminologies).

Device Language Message Specification (DLMS) with functionalities of Companion Specification for Energy Metering (COSEM) based on open protocols and maintained by Device Language Message Specification User Association, DLMS UA, Geneva, in the form of four technical Reports, namely “Blue”, “Green”, “Yellow” and “White” Books, have been adopted by IEC on regular basis in the International Standards mentioned above for interoperable use of electricity meters in a data network. The continuous development of DLMS/COSEM open communications protocols for data retrieval, updation, and reconfiguration of metering devices, has enabled diverse operators to access safely and quickly data from metering equipment provided by diverse manufacturers.

This standard, a Companion Specification in the form of a Guide, is intended to provide a field level basis for efficient and secure transfer of electricity metering data in an open manner with judicious application of features and protocols of the International Standards.

This specification refers to the latest updates of Interface classes and OBIS codes available in 9th edition (2009) of the Blue Book of DLMS UA. This also refers to updates of procedures and services available in 7th edition (2009) of the DLMS UA Green Book. These revised Technical Reports of DLMS UA, considered as pre-standards for several parts of IEC 62056, will be adopted by IEC in due course and subsequently by BIS in adopted Indian Standards being published. Till such time these books, accessible by members of DLMS User Association in

(*Continued on third cover*)

***Indian Standard***

**DATA EXCHANGE FOR ELECTRICITY METER**

**READING, TARIFF AND LOAD CONTROL —**

**COMPANION SPECIFICATION**

1 SCOPE

**1.1** This standard is intended for use as companion to IS/IEC 62056 (Parts 21, 42, 46, 47, 53, 61 and 62) series of standards on ‘Electricity metering: Data exchange for meter reading, tariff and load control’ for proper application/implementation of the provisions thereof.

**1.2**  These generic metering data exchange standards based on DLMS/ COSEM open protocols and features, provide a coverage for structured modeling of metering functionalities as available at communication interface(s), with procedures for identification of these data objects by mapping into respective codes, and finally for direct local exchange or remote exchange of these data messages by transporting over various layers of communication channels with specified procedures and services, as applicable.

**1.3** This Companion Specification provides guidelines, specifies optional DLMS / COSEM elements and outlines boundary requirements for design of such DLMS / COSEM compliant electricity meters for possible applications in Indian electricity networks (*see* also Annex A). Such selections may involve:

1. COSEM interface classes, their instances, attributes and methods to be supported, event and status tables, identified objects, DLMS services, communication media and protocol stacks.
2. Requirements for Direct Local Data Exchange involving HHU (MRI) and Remote data exchange with HOST Computer.
3. The necessary country / project specific codes, not documented by DLMS UA, are included in Annex A for specified usage of electricity meters.
4. For requirements of data exchange for smart meters [*see* IS 15959 (Part 2): 2016 Data exchange for electricity meter reading, tariff and load control — Companion specification for smart meters].

**1.4** The following are outside the scope of this standard and will be decided by user/ manufacturer/ system integrator:

1. Host computer – Metering equipment connectivity;
2. Compatible modem (Data Communication Equipment) and its requirements for chosen communication medium; and
3. Values and distribution methods of secret keys.

**1.5** Metering functions are outside the scope of this standard and are covered by prevailing Indian Standards as applicable.

2 REFERENCES

 The standards listed in Annex H contain provisions which, through reference in this text, constitute provisions of this standard. At the time of publication, the editions indicated were valid. All standards are subject to revision and parties to agreements based on this standard are encouraged to investigate the possibility of applying the most recent edition of the standard indicated at Annex H.

|  |  |
| --- | --- |
|  |  |
|  |  |

3 TERMINOLOGIES

 For the purpose of this standard, the definitions given in IS/IEC/TR 62051-1 and the following shall apply.

* + 1. Network-

A data communications system that allows a number of devices to communicate with each other. It indicates interconnection of these devices in a way concordant with the communications profile selected. It does not necessarily mean a diverse or wide-ranging set of connections, nor any routing capability (*see also* **13.23** of IEC 62051).

* + 1. Architecture-

Overall requirement and application of the communication network, indicating structure and hierarchy (*see also* **4.3** of IEC 62051).

* + 1. Object-

A collection of characteristic attributes and specified methods (*see also* DLMS UA, Blue Book).

* + 1. Object Modelling-

A technologically independent model of a meter can be represented by a list of objects as seen through an interface and provides controlled access to their attributes and methods. The data objects related to metering functionalities and parameters can be mapped into identifier codes forming a message for transportation according to an open protocol (*see also* DLMS UA, Blue Book).

* + 1. Access Point-

A physical interface point used to transfer data from/ to the meter network. It may be a gateway from a LAN to a higher order network or an interface to temporary reading equipment such as a HHU (MRI), a portable PC, etc (*see also* **4.2** of IEC 62051).

* + 1. Hand Held Unit (HHU)-

A portable device for reading and programming equipment or meters at the access point (*see also* **4.19** of IEC 62051 and Annex J).

* + 1. Meter Reading Instrument-

These are synonymous with HHU (*see also* **G-1.7** & **G-1.8** of IS 14697).

* + 1. Configuration-

Setting of measurement and communication parameters to operate the meter correctly. (*See also* **4.7** of IEC 62051)

* + 1. Protocol-

The rules for communications system operation that must be followed if communication is to be affected (for example for meter reading and programming) (*see also* **13.72** of IEC 62051).

* + 1. Open Protocol-

The rules for communications system operation suitable for meter reading and limited programming of meters and data collection equipment of different types and from different manufacturers through open standardized documents, for example DLMS/ COSEM (*see also* **3.1.65** of IS/IEC 62051-1).

* + 1. Interface-

A point or means of interaction between two systems (for example between a meter and a data collection equipment) (*see also* **13.50** of IEC 62051).

* + 1. Parameter-

A single identifiable metering or other quantity which may be read or altered within meter readings, tariffication, or control and may have multiple aspects such as its value, scaling, timestamp, etc.

* + 1. Parameterization-

Setting of those parameters that define the configuration of the metering device, which implies writing values of COSEM object attributes. The parameterization tool can be seen as a special client.

* + 1. Data Concentrator-

A device used to hold the data from a number of meters, in a way that identifies the data from each meter and allows it to be accessed in real time by a higher-level data collector. Typically, a concentrator is accessed in a manner similar to the meters, but supports faster or cheaper communication, and has greater storage capacity than available with the meters themselves (An example of use is to concentrate data from a number of electrical distribution substations).

* + 1. HOST Computer-

A computer system to which data collected by HHUs is returned for processing, and /or which can collect data remotely from a meter or data concentrator.

* + 1. Data Encryption-

The changing of the form of a data stream in such a way that only the intended recipient can read or alter the information and unauthorized messages may be detected. It ensures data security (*see also* **13.29** of IEC 62051).

* + 1. Key-

Transforms a particular message using an algorithm to make it unreadable to anyone except the recipient, to preserve integrity, authenticity and confidentiality of the message or vice versa, through a standardized procedure. (*See also* DLMS UA, Green Book).

* + 1. Confidentiality-

Preserving authorized restrictions on information access and disclosure, including means for protecting personal privacy and proprietary information. A loss of confidentiality is the unauthorized disclosure of information (*see also* NIST FIPS PUB 199: 2004).

* + 1. Integrity-

Guarding against improper information modification or destruction and includes ensuring information non-repudiation and authenticity. A loss of integrity is the unauthorized modification or destruction of information (*see also* NIST FIPS PUB 199: 2004).

* + 1. Open Systems Interconnections (OSI)-

 A framework for communication processes in which the process is divided into seven functional layers, arranged one above the other with each having a separate responsibility. Each layer communicates with the layer immediately above and below it (*see also* **12.1** & **12.4** of IEC 62051).

* + 1. Collapsed Architecture-

A subset of the OSI reference model which consists of only three layers: Physical layer, Data link layer and Application layer.

* + 1. Layer-

One of seven functional entities within the OSI model (normal and collapsed architecture) as given in Table 1 (*see also* **12.2** of IEC 62051).

**Table 1 OSI model- Functional Layers**

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl.No** | **Layer** | **Normal** | **Collapsed** |
|  |  |  |  |
|  | 7 | Application | Application |
|  | 6 | Presentation | \_ |
|  | 5 | Session | \_ |
|  | 4 | Transport | \_ |
|  | 3 | Network | \_ |
|  | 2 | Data-link | Data-link |
|  | 1 | Physical | Physical |

3.22.1 Physical Layer (OSI Layer 1)-

The layer of the OSI reference model which provides bit transmission between one node and the next, physical interfacing with media, data signal encoding and defines electrical parameters, connector size, shape and pinouts.

3.22.2 Data Link Layer (OSI Layer 2)-

That layer of the OSI reference model which performs, and controls specified transmission service functions by means of a link protocol.

3.22.3 Network Layer (OSI Layer 3)-

That layer of the OSI reference model which establishes the source to destination path across the network, switches, routes and controls congestion of information packets.

3.22.4 Transport Layer (OSI Layer 4)-

That layer of the OSI reference model which provides reliable transmission of layer 7 messages end-to-end across the communication network.

3.22.5 Session Layer (OSI Layer 5)-

That layer of the OSI reference model which establishes and terminates end-to-end sessions, provides process synchronization, and determines if half-duplex or full duplex is to be used.

3.22.6 Presentation Layer (OSI Layer 6)-

That layer of the OSI reference model which establishes the syntax (form) in which data is exchanged.

3.22.7 Application Layer (OSI Layer 7)-

That layer of the OSI reference model which provides end –user services such as file transfers, electronic messages and remote data base access.

* + 1. Conformance Testing-

Planned and regulated process of evaluation of a type of metering equipment in order to gain confidence about implementation of declared features of this standard and generic standards IEC 62056 in that particular type, by a laboratory authorized for the purpose (*see also* DLMS UA, Yellow Book and Annex K).

* + 1. Interpretation of Symbols

All the symbols should be interpreted as per general mathematics standard: like ‘/’ means OR.

NOTE - Wherever the words ‘Interface class No./Attribute’ appear in the standard, they shall be read as ‘Interface class no. and Attribute’.

* + 1. RTC default time format shall be 24 h
1. ARCHITECTURE

**4.1** The typical connectivity scheme between a meter (server) and the client, considered for this standard, is shown in Fig. 1.

Meter Category A/ B/ C

(Server)

DC

**Legend**

DCE – Data communication equipment

 PSTN Modem, GSM/GPRS Modem

HHU – Hand held unit

DC – Data Concentrator

P1 – RS 232/RS 485 Port – For remote access

P2 – Optical Port – For local access

HHU

Link to base computer system

1-1 HDLC PORT.

DCE

1-1 HDLC PORT.

P1

 P2

HOST

(Client)

BCS

1-1, HDLC PORT.

FIG. 1 MESSAGE FLOW CONNECTIVITY SCHEME BETWEEN METER/SERVER AND CLIENT

* 1. Physical Requirements

 Overall purpose and software objectives are described

All categories of meter (server) shall support at least one communication port as given at P2 below:

* + 1. P1 – An Electrical port compatible with RS 232 or RS 485 specifications. This shall be used for remote access from the HOST (Client) or DC (Client).
		2. P2 – An Optical port complying with hardware specifications detailed in IS/IEC-62056-21. This shall be used for local access from an HHU (MRI).
		3. The P1 and P2 both shall support the 3-layer Connection Oriented COSEM/HDLC profile, with a minimum and default baud rate of 9600.
		4. Both P1 and P2 shall support 4 byte and one byte addressing both. HHU can read from either port.

The optical port is not required to support any mode of IS/IEC-62056-21, that is, mode of usage shall be direct HDLC (*see also* Fig. 1).

* 1. Requirements for Simultaneous Operation

The meter (server) is not required to allow more than one association to be open at any one time. Optical port shall have priority when both ports are accessed simultaneously. This means that if the electrical port is connected and being accessed for data, any attempt to connect on optical port shall cause the connection on electrical port to be interrupted and the optical connection processed after sending ‘DM’ (Disconnected Mode) message to HOST. Any further attempts to communicate on electrical port while the optical port is being used shall be returned with a ‘DM’ code. This is an indication to the HOST that the meter is temporarily busy. Simultaneous operation test is applicable only for meters with P1 and P2 ports.

NOTE — wherever there is a requirement for simultaneous operation from utility, the same may be agreed between buyer and supplier.

1. LOGICAL STRUCTURE OF METERS

The meter represents one physical device as mentioned in **4.5** of IS/IEC 62056-6-2.

The physical device (meter) hosts one logical device as mentioned in **4.5** of IS/IEC 62056-6-2, which is the Management logical device. This has SAP (Service Access Point) address 1, as mandated in IS/IEC 62056-53. The physical device address (lower HDLC address) shall also be set to a default value of ‘256’ on supply and the actual communication address shall be programmed on installation.

The meter shall support the Logical Name (LN) referencing mechanism as defined in Annex C.1 of IS/IEC 62056-6-2. Short name referencing as defined in Annex C.2 of IS/IEC 62056-6-2 is not required to be supported.

The meter shall support three associations in the Management Logical Device

1. Public client association (PC);
2. Meter reader association (MR); and
3. Utility settings association (US).
	1. Mandatory Objects

The following objects as given in Table 2 are mandated by IS/IEC 62056-6-2.

**Table 2 Mandatory Objects**

(*Clause* 5.1)

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Sl.No** | **Object** | **OBIS Code** | **Interface Class** | **Requirements** |
|  |  |  |  |  |
|  | Logical device name | 0.0.42.0.0.255 | IC = 1 (Data) | Value data type will be octet-string with maximum length 16. |
|  | Current association | 0.0.40.0.e.255 | IC = 15 (Association LN) |  e = 1 for PC, e = 2 for MR and e = 3 for US. The meter shall have three association objects, of which the currently connected one shall be accessible via the OBIS 0.0.40.0.0.255 |
| NOTES**1** The Logical Device name shall have a maximum length of 16 characters and shall have as its first three characters the manufacturer’s 3-letter code as specified in 4.6.2 of IS/IEC-62056-6-2. **2** The three letters Manufacturer IDs are administered by the FLAG Association, in co-operation with the DLMS-UA.3 For meters with RS485 port, the physical device address shall be assigned using OBIS code 0.0.22.0.0.255 and IC = 23. The effectiveness of the address change shall take place after the termination of the current association. Physical device address change can be done using 1 byte addressing. |

* 1. Association Properties

**5.2.1** The PC association shall contain the following in addition to mandatory objects:

a) Meter’s real-time clock; and

b) Meter serial number.

**5.2.2** The MR association shall contain the following in addition to mandatory objects:

a) Profile objects allowing bulk collection of data defined by the parameter lists in Annex C, D, E, F and G; and

b) Simple objects allowing ad-hoc access to items in the instantaneous parameters list. Ad-hoc access to the profile objects shall also be possible.

**5.2.3** The US association shall contain in addition to mandatory objects:

a) All the objects accessible via the MR association; and

b) Simple and compound objects allowing tariffication and configuration of the meter (*see also* 9).

**5.2.4** The object list of each association is detailed in Annex C, D, E, F and G. Mandatory objects do not necessarily appear in these tables. Access rights for each data item are also shown in Annex C, D, E, F and G. The association properties, object list, and access rights are identical on ports P1 and P2.

**5.2.5** The required associations shall have the properties as given in Table 3.

**Table 3 Association Properties**

(*Clause* 5.2.5)

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Sl No** | **Feature** | **Public Client** | **Meter Reader** | **Utility Settings** |
|  |  |  |  |  |
|  | SAP Address pair in format (client, server) | (16,1) | (32,1) | (48,1) |
|  | Application Context – Basic security | LN without ciphering | LN without ciphering | LN without ciphering |
|  | Application Context – Advanced security | Not applicable | LN-Ciphered | LN-Ciphered |
|  | Sign on Authentication Mechanism (*see also* 7.3.7.2 of IS/IEC-62056-53 | Lowest Level | Low Level (LLS) | High Level (HLS) |
|  | Services required in conformance block. |  Get | Get, Set, Get with block transfer, selectiveaccess. | Get, Set, Action, Get and Set with block transfer, Selective access |
|  | OBIS codes | 0.0.40.0.1.255 | 0.0.40.0.2.255 | 0.0.40.0.3.255 |

NOTE — Programmability is applicable only for meters with RS 485 ports. Hence, in MR mode ‘Set’ is applicable only for RS 485 meter.

* 1. Descriptive Notes for Logical Structuring
		1. *Associations*

Each Logical device can organize the data objects into different associations, each having different access rights to the list of objects. Each association defines the SAP address pair of the client and server logical device addresses that participate in the data transaction.

* + 1. *Objects*

All meter data is represented by COSEM Interface objects. COSEM interface objects are instances of the COSEM Interface classes.

* + 1. *Attributes & Methods*

The actual placeholders of the different data elements of the meter are the attributes of the objects, whereas the methods exposed by the objects allow manipulating the attributes in defined manners.

* 1. Referencing Methods

**5.4.1** DLMS/COSEM provides two referencing methods to access the meter data, Logical name referencing and Short name referencing. Under LN referencing, data is accessed by specifying the Logical name (OBIS code) of the object, the Class ID and the attribute (or method) index. Under SN referencing each attribute and method of each object has its own individual address.

**5.4.2** Access rights are specified for each attribute and each method of every data object in the meter. Attributes may have the following access rights:

1. No access;
2. Read access;
3. Write access; and
4. Read-write access.

**5.4.3** Methods may have the following access rights

1. No access; and
2. Execute access

**5.4.4** Access rights are specific to each association. Different associations may have different object lists, or award different access rights to the same set of data objects. Thus, the grouping of data into associations gives different views of the same real data.

1. USAGE OF DLMS / COSEM PROVISIONS
	1. Usage of Interface Classes

**6.1.1** This standard defines the set of Interface Classes to be used for various types of data. The interface class for the identified parameters is specified in Annex C to Annex G.

**6.1.2** Either requiring support or offering support for a class shall not imply support for all its attributes. Required attributes are listed under respective Annex as Notes. Not supporting an attribute can be implemented as given below:

1. Attribute does not appear in the object list; and
2. Attribute appears in the object list but with no access rights.

**6.1.3** Attribute\_0 referencing (indicating access to all attributes in one request, as specified by Bit 10 of the conformance block) is not required to be supported in any case.

**6.1.4** References to classes may be made in the form of capture-IDs or register-table entries even if the corresponding classes are not supported for direct data access.

**6.1.5** References to OBIS codes may be made in the form of capture-IDs, masks, or scripts even if the corresponding objects are not individually accessible. In this case those items will not appear in the Association object.

* 1. Requirements for Interoperability

**6.2.1** A client device supporting the parameters, functions, and classes of the Minimum Specification, along with suitable configuration of system-dependent features (such as physical addresses, timeout thresholds, and secret keys), shall be able to retrieve all of the specified data items and perform any of the specified updates without particular knowledge about the server.

**6.2.2** Given the knowledge that a certain client or a certain server implements particular additional features defined as in this standard, a server can be built to return data and receive updates from that client, or a client can be built to retrieve data and perform updates upon that server, respectively, without further special knowledge other than system-dependent features.

**6.2.3** Interpretation of the data shall be possible by any user with adequate knowledge of electricity metering provided that a complete set of data has been retrieved.

* 1. Country-Specific OBIS Codes

Within this Companion Specification, country-specific variations or additions to quantities such as energy types are managed by the allocation of new codes in the full OBIS format. The country-specific OBIS codes introduced in this document are in the format - a.b.94.91.e.f, along with interface class and attributes, where C=94 indicates a country-specific code and D=91 is allocated for India.

1. ASSOCIATION AND DATA SECURITY

As per the provisions of the DLMS/COSEM protocol, Data access control mechanism and encryption/authentication mechanism shall be supported. Access control mechanisms shall be used in the association establishment phase and encryption/ authentication mechanism shall be used in the Data communication phase.

* 1. Security Profiles

Two security schemes are defined in this standard.

* + 1. *Basic Security*

The basic security profile does not provide for encryption or authentication during data communication stage. The only security provided for is the sign-on authentication security provided by low level and high-level security as applicable for the respective associations.

* + 1. *Advanced security*

Encryption, authentication, or both can be performed by the application program and transferred using ciphered PDUs. All systems must implement basic security. Implementation of advanced security is discretionary. When implemented it shall be as provided in NIST SP 800-38-D

* 1. Security setup (class\_id: 64, version: 0)

The following interface class is defined in addition to those published in the National/ International standard (*see* *also* IS/IEC 62056-6-2).

Instances of this IC contain the necessary information on the security policy applicable and the security suite in use within a particular AA, between two systems identified by their client system title and server system title respectively. They also contain methods to increase the level of security and to transfer the global keys as given in Table 4.

**Table 4 Security Setup**

|  |  |  |
| --- | --- | --- |
| **SI No. Security Setup** | **0….n** | **Class\_id = 64,version = 0** |
|  |  | Data Type  | Min. | Max. | Def.  | Short Name |
| (1) i)Attributes |  |  |  |  |  | (7) |
|  | logical name  | (static) | octet-string | - |  - | - | x |
|  | security-policy | (static) | enum | - | - | - | x + 0×08 |
|  | security-suite | (static) | Enum | - | - | - | x + 0×10 |
|  | client-system-title | (dynamic) | octet-string | - | - | - | x + 0×18 |
|  | server-system-title | (static) | octet-string | - | - | - | x + 0×20 |
| ii) Specific Methods |  | m/o |  |  |
|  | security\_activate | o |  | x + 0×28 |
|  | global\_key\_transfer | o |  | x + 0×30 |
| NOTE: Use of this interface class is only required for Advanced Security profile implementations. Implementations of Basic Security profiles shall not contain this, Class. |

* 1. Security Setup objects
		1. The following object identifiers as given in Table 5 are defined in addition to those given in IS/IEC 62056-6-2.

**Table 5 Object for Security Setup**

|  |  |  |
| --- | --- | --- |
| **Security Setup Objects** | **IC** | **OBIS code** |
| A | B | C | D | E | F |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Security Setup | 64 – Security Setup | 0 | b | 43 | 0 |  e | 255 |

**7.3.2** Instances of the IC Security setup are used to set up the message security features. For each Association object, there is one Security setup object managing security within that AA. Value group E numbers the instances. This specification defines 2 values for E corresponding to the 2 associations as given in Table 6.

**Table 6 Security Setup Object OBIS Code for Association Levels**

(*Clause* 7.3.2 and 7.4.1)

|  |  |  |
| --- | --- | --- |
| **Sl No** | **Security Setup Object OBIS Code** | **Association Description** |
| (1) | (2) | (3) |
|  | 0.b.43.0.2.255 | Meter Reader Association |
|  | 0.b.43.0.3.255 | Utility Settings Association |
| NOTE These instances of the Security Setup interface Class are only required for Advanced Security profile implementations. Implementations of Basic Security profile shall not contain these instances. |

* 1. LN Association Interface Class

**7.4.1** This standard utilizes version 1 of the Association LN Interface Class (IC 15). Version 1 of IC=15 adds an extra attribute ‘security\_setup\_reference’ (attribute 9) which will be used to contain the reference to an instance of a Security Setup class, namely one of the two instances defined in Table 6.

**7.4.2** The implementation of version 1 of Association LN Interface class is not required for Basic Security profile.

**7.4.3** The following Interface Class definition is defined in Table 7 in addition to those published in IS/IEC 62056-6-2.

**7.4.4** COSEM logical devices able to establish AAs within a COSEM context using LN referencing model the AAs through instances of the ‘Association LN’ IC. A COSEM logical device has one instance of this IC for each AA the device is able to support.

**Table 7 LN Association Interface Class**

(*Clause* 7.4.3)

|  |  |  |
| --- | --- | --- |
| **SI No. Association LN**  | **0….MaxNbofAss** | **Class\_id = 15,version = 1** |
|  |  | Data Type | Min. | Max. | Def. | Short Name |
| (1)i) Attributes: | (2) |  (3) | (4) | (5) | (6)  | (7) |
|  | logical\_name (static) | octet-string | - | - | - | x |
|  | Object\_list (static) | object\_list\_type | - | - | - | x + 0×08 |
|  | associated\_partners\_id | associated\_partners\_type | - | - | - | x + 0×10 |
|  | application\_context\_name | application\_context\_name | - | - | - | x + 0×18 |
|  | xDLMS\_context\_info | xDLMS\_context\_type | - | - | - | x + 0×20 |
|  | authentication\_mechanism\_name | Mechanism-name | - | - | - | x + 0×28 |
|  | LLS\_secret | octet-string | - | - | - | x + 0×30 |
|  | association\_status | enum | - | - | - | x + 0×38 |
|  | security\_setup\_reference (static) | octet-string | - | - | - | x + 0×40 |
| ii) Specific Methods: |  | m/o |  |  |
|  | reply\_to\_HLS\_authentication(data) | o |  | x + 0×60 |
|  | change\_HLS\_secret(data) | o |  | x + 0×68 |
|  | add\_object(data) | o |  | x + 0×70 |
|  | remove\_object(data) | o |  | x + 0×78 |

* 1. Descriptive Notes for Data Security
		1. *Access Control for Association*

The DLMS/COSEM standard provides three different sign-on authentication mechanisms for each association’s access to meter data applied at the time of performing COSEM OPEN operation.

* + - 1. Lowest level security

Open access without any authentication at sign-on. This shall be used by the public client.

* + - 1. Low level security (LLS)

Password based sign-on where the client authenticates itself to the meter using a password. The Utility Settings association shall provide access to write the password for all associations that utilize this authentication scheme (Currently only the Meter Reader association object). This is accomplished by providing write access to the ‘LLS\_secret’ attribute (attribute number 7) of the Meter Reader association LN object. This write access is provided only through the Utility Settings association.

The MR association object has an OBIS code 0.0.40.0.2.255. The LLS\_ secret of this object shall be changed only through the US association.

* + - 1. High level security (HLS)

HLS mechanism defines a 4-pass sign-on scheme where the client and server exchange challenges (a random number or code) and then reply to the challenges with a processed response. The processing performed on the challenges is an encryption using a secret ‘key’. The Utility Settings association shall provide write access to the ‘secret’ attribute of the Utility Settings association. The US association object has an OBIS code 0.0.40.0.3.255. The HLS secret of this object can be changed using method 2 of this object. The encryption mechanism used for processing the challenges shall be AES-128 algorithm as provided in NIST FIPS PUB 197:2001. HLS Authentication Mechanism Id (2) needs to be implemented.

* + 1. *Encryption for Data Communication*

The confidentiality of data communicated between the meter and the client is handled by the encryption mechanism chosen in the Application Context. Associations utilizing the ‘Logical Name with ciphering’ application context provide encryption/decryption services for data messages. Ciphering may be:

a) Authentication, providing message integrity;

b) Encryption, providing confidentiality; and

c) both.

1. EVENT HANDLING

This clause adds the definitions for the event code object and event log object.

* 1. Event Code

**8.1.1** An event code object is used to hold the identifier corresponding to the most recent event. Data, register or extended register classes can be used to model this object. DLMS allows defining a country specific reference table that lists all possible events with corresponding identifiers (*see* Annex G). For the purposes of this Specification the Interface Class used for this object is restricted to IC=1 (Data) as given in Table 8. The value attribute of the object will have a DLMS data type ‘long unsigned’ (16-bit integer) which will contain the event identifier for the last recorded event (identifier taken from the reference tables (*see* Annex G).

**Table 8 Event Code**(*Clause* 8.1.1)

|  |  |  |
| --- | --- | --- |
| **Event code** | **IC** | **OBIS code** |
| A | B | C | D | E | F |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Event code | 1 – Data | 0 | b | 96 | 11 |  e | 255 |

**8.1.2** Value group E allows to classify events into different categories as needed. Currently DLMS allows 10 values (0...9) for value group E, enabling user to define up to 10 event categories.

**8.1.3** This standard defines 7 categories for classification of events and correspondingly 7 event code objects as given in Table 9.

**Table 9 Event Code OBIS Codes**

|  |  |  |
| --- | --- | --- |
| **Sl.No.** | **Event Code object OBIS Code** | **Event Category Description** |
|  |  |  |
|  |  |  |
|  | 0.b.96.11.0.255 | Voltage related events |
|  | 0.b.96.11.1.255 | Current related events |
|  | 0.b.96.11.2.255 | Power failure related events |
|  | 0.b.96.11.3.255 | Transaction related events |
|  | 0.b.96.11.4.255 | Other events |
|  | 0.b.96.11.5.255 | Non-rollover events |
|  | 0.b.96.11.6.255 | Control events for connect/disconnect |
| NOTES**1)** The 7th Event code object is required only where remote load control by means of connect/disconnect are specified by agreement between the Utility and the manufacturer. **2)** Reference to Annex G and the relevant tables may be made for the valid Event Identifier values defined for the above 7 categories by this standard. |

* 1. Event Log

**8.2.1** An event log is a profile generic object provided to store historical values of the event code object for a given category of event as given in Table 10. The capture object includes object attribute definitions of associated data. Associated data includes event code and other relevant information such as timestamp, instantaneous electricity related information (such as current/voltage/energy register, contents etc at the time of the event).

**8.2.2** For the purpose of this standard, the capture objects will include the entries specified in Annex G.

**Table 10 Event Log Profile**

(*Clause* 8.2.1)

|  |  |  |
| --- | --- | --- |
| **Event Logs** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Event log | 7 – Profile Generic | 0 | b | 99 | 98 | e | 255 |

**8.2.3** Value of group E allows to classify event logs into different categories as needed. Currently DLMS allows 10 values (0...9) for value group E allowing to define up to 10 event log categories as given in Table 11.

**8.2.4** This standard defines 7 categories for classification of event log objects with a one-to-one correspondence with the 7 event code categories defined in 8.1.

* + 1. *Event Log Storage Recommendations*

This standard recommends a total storage of 200 events in the event logs. The division of the specified storage space across the 7 compartments specified above shall be by the agreement between the utility and the manufacturer.

The event code and event log parameters are accessible through the MR and US associations with read-only access (*see* Annex J).

**Table 11 Event Log OBIS Codes**

(*Clause* 8.2.3)

|  |  |  |
| --- | --- | --- |
| **Sl No** | **Event Log Object OBIS Code** | **Event Category Description** |
| (1) | (2) | (3) |
|  | 0.b.99.98.0.255 | Voltage related events |
|  | 0.b.99.98.1.255 | Current related events |
|  | 0.b.99.98.2.255 | Power failure related events |
|  | 0.b.99.98.3.255 | Transaction related events |
|  | 0.b.99.98.4.255 | Other events |
|  | 0.b.99.98.5.255 | Non-rollover events |
|  | 0.b.99.98.6.255 | Control events for connect/disconnect |
| NOTE -The 7th Event log category is required only where remote load control by means of connect/disconnect are specified by agreement between the Utility and the manufacturer |

1. TOU METERING

**9.1** DLMS/ COSEM provides a number of interface classes to deal with TOU metering. These include activity calendars (objects that specify the time-switches for tariffs based on a season, week, day profile tree) and schedules (a simple tabular listing of time-switch scripts associated with a date-time).

**9.2** These objects associate a script (stored in a script table object, IC=9) with each time-switch. The script usually defines the list of registers that get enabled for that time-switch using a register activation object (IC=6) that stores masks of registers that can be selectively enabled/disabled.

**9.3** For the purpose of this standard, the activity calendar (IC=20) shall be used as given in Table 12.

**Table 12 Activity Calendar OBIS Code**

(*Clause* 9.3)

|  |  |  |
| --- | --- | --- |
| **Activity Calendar** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Activity Calendar | 20 – Activity Calendar | 0 | b | 13 | 0 | 0 | 255 |

**9.4** An instance of a Script Table class, the tariffication script table object will be used to store the scripts related to each time-switch in the schedule as given in Table 13.

**Table 13 Tariff Script Table OBIS Code**

(*Clause* 9.4)

|  |  |  |
| --- | --- | --- |
| **Script Table** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Tariffication Script Table | 9 – Script Table | 0 | b | 10 | 0 | 100 | 255 |

**9.5** This standard utilizes a simple mechanism for associating TOU/ TOD scripts with Tariffs, as described below. Use of the Register Activation object is not required.

**9.6** Under this mechanism, script identifiers in the tariffication script table are inherently associated with tariffs, as defined below.

**9.7** Script identifiers from 1 to 16 are associated with the Activation of Tariff Rate Registers 1 to 16. Implementations that do not require 16 different tariff rates shall use identifiers from 1 to the required number. For example, if 8 tariffs are defined, script identifiers 1 to 8 shall be used, where scripts 9 to 16 are reserved for future use. Scripts identifiers 17 to 32 are associated with Maximum Demand tariffs 1 to 16. Implementations that do not require 16 different tariff rates shall use identifiers from 1 to the required number.

**9.8** The activity calendar shall be used to associate activation times to different Tariff rates simply by using the appropriate script identifiers. All scripts shall point to a dummy OBIS code and attribute index which has no associated meaning.

**9.9** To ensure coordination of the updates to various attributes, activity calendar shall be updated by writing to the passive-calendar attributes. The end of the update process is indicated by update of the activation date attribute with an appropriate value, causing all changes to become effective simultaneously.

**9.10** Use of the special days table is not considered presently in this standard.

1. BILLING PERIODS

**10.1** Billing period resets are driven by an instance of the single action schedule class in conjunction with a script table. The Data of the Billing Period is stored in a Profile Generic object as given in Table 14. Each entry in the profile buffer captures the billing period values for a specific Billing Period.

**Table 14 Billing Period OBIS Code**

|  |  |  |
| --- | --- | --- |
| **Profile Generic** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Data of Billing Period Profile | 7 – Profile Generic | 1 | b | 98 | 1 | 0 | 255 |

**10.2** This standard specifies the single action schedule object to drive the end of billing period resets as given in Table 15. The object will contain the time-date entries at which billing period resets are scheduled.

**Table 15 Single Action Schedule OBIS Code**

|  |  |  |
| --- | --- | --- |
| **Single Action Schedule** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| MDI Reset / End of Billing Period | 22 – Single Action Schedule | 0 | b | 15 | 0 | 0 | 255 |

**10.3** Each time-date entry in the execution time array will be associated with a link to a single Script in the MDI Reset/end of billing period script table. The Script table object as given in Table 16 will be programmed with scripts to handle the Billing period resets.

**Table 16 Billing Script Table OBIS Code**

|  |  |  |
| --- | --- | --- |
| **Script Table** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| MDI Reset / End of Billing Period Script Table | 9 – Script Table | 0 | b | 10 | 0 | 1 | 255 |

**10.4** The script table will contain a single script that specifies the capture method invocation for the corresponding data of billing period profile (1.0.98.1.0.255).Therefore a single action schedule entry will trigger a call to the Script table to execute the capture method at a specific time (namely the end of the billing period) which will cause a billing period entry to be made in the profile for the current period and trigger the start of a new billing period. Other actions internal to the meter may also be triggered by the end of each billing period but are not required to be expressed as scripts here.

1. HISTORIC DATA

**11.1** Historic data can be accessed by two mechanisms in DLMS-COSEM. One mechanism provides access to past values of specific quantities by using a VZ (billing period number) related value for F in the OBIS code of the original quantity. The other mechanism is profile generic objects, where individual billing data set is one entry. Profile generic object method is supported in this specification for accessing historical data.

* 1. Billing Period Counter

**11.2.1** The meter will contain an instance of a billing period counter object as given in Table 17.

**Table 17 Billing Period Counter OBIS Code**

|  |  |  |
| --- | --- | --- |
| **Billing Period Counter** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Billing Period Counter | 1 – Data | 0 | b | 0 | 1 | 0 | 255 |

**11.2.2** The value attribute of the object will have a cumulative value since manufacturing. The meter will contain an instance of a Data object that provides the number of available billing periods in the meter as given in Table 18.

**Table 18 Available Billing Periods OBIS Code**

|  |  |  |
| --- | --- | --- |
| **Number of Billing Periods** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Available Billing periods | 1 – Data | 0 | b | 0 | 1 | 1 | 255 |

**11.2.3** The above can be read by the client to identify how many previous billing period data is available in the meter.

* 1. Profiles

**11.3.1** Historic data like load profiles etc are supported in IEC 62056 by the Profile Generic Interface Class (IC=7). This object supports capture of other meter object attributes at specific intervals or on demand. The captured data is stored in the buffer attribute (Attribute 2) of the Profile generic class. This class also supports Selective access to filter the buffer data in response to GET requests. There are two mechanisms for selective access viz. selective access by entry and selective access by range.

**11.3.2** This standard requires that the selective access by range shall be supported for block load profile and daily load profile. This standard requires support for selective access by entry for billing data profile and event log profiles.

**11.3.3** In case of selective access by range, this standard imposes that the restricting object is to be an instance of the clock interface class (IC=8) and the date-time attribute of the object is captured in the buffer.

**11.3.4** Selective access by entry and range supports filtering the profile buffer by rows as well as by columns. However, this standard doesn’t require support for filtering by columns (*see also* Annex L).

**11.3.5** Any configuration change in profile capture object will be treated as given in 5.6 of IS/IEC 62056-6-2.

**11.3.6** The values of a capture object of a profile may be replaced by null data, if it can be unambiguously recovered from the previous value (for example time stamp in block load profile: it can be calculated from the previous value and capture period).

Similarly, compact-array or array can be used with or without null data for example for string type data (Real Time Clock Stamp) compact array with Null data can be used.

Null data and compact array is an optional feature to be mutually agreed between the meter manufacturer and the meter reading software implementer.

1. COMMUNICATION PROFILES

IEC 62056 adopts the collapsed architecture subset of the open systems interconnect reference model. Figure 2 illustrates the system used. This standard requires that the three-layer serial Connection-Orientated (CO) profile shall at least be supported.

The 3-layer serial CO profile consists of COSEM, logical link control (LLC), and high-level distribution line control (HDLC) on a serial physical channel. This profile may be extended by using modems to handle different carriers such as PSTN, GSM, or GPRS, Radio, Zigbee etc, by tunneling HDLC frames over these media.

The addition of dial-up modem connections as described in IS/IEC 62056-42 is required only where the modem is fitted internally to the meter.



Fig. 2 COMMUNICATION PROFILE OPTIONS

1. COMMUNICATION SETUP OBJECTS

This standard requires the communication setup objects as given in Table 19 to be supported in the meter implementation. This document also recommends that a specific baud rate may be fixed between the utility and the manufacturer for each project. The suggested default baud rate is given in 4.2.

**Table 19 Communication Setup Object**

|  |  |  |
| --- | --- | --- |
| **Communication Setup and Related Objects for Serial Communication** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| IEC HDLC Setup | 23 - IEC HDLC Setup | 0 | b | 22 | 0 | 0 | 255 |

1. CONNECT/DISCONNECT CONTROL

In implementations that require remote Connect/Disconnect control, effected by operation of an output pulse from the meter, this specification requires support for the disconnect class object as given in Table 20.

**Table 20 Disconnect Control Object**

|  |  |  |
| --- | --- | --- |
| **Disconnector** | **IC** | **OBIS Code** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| Disconnect Control | 70 – Disconnect Control | 0 | b | 96 | 3 | 10 | 255 |

**ANNEX A**

(*Clause* 1.3)

**INTRODUCTION TO METERING PARAMETERS WITH DATA**

**IDENTIFIERS**

**A-1** Three categories of electricity meters have been selected for compiling comprehensive lists of metering parameters with their data identifiers as required for data networks in India for COSEM procedures and services. The relevant reference documents are listed in Annex H.

**A-1.1 Category A Meter**

This meter is identified for use at sub-station feeders and Distribution Transformer Centers. The parameters listed for this category are for ‘Energy Accounting and Audit’ purposes (*see* also Annex C).

**A-1.2 Category B Meter**

This meter is identified for use at meter banks and network boundaries. The parameters listed for this category are for import / export of energy. This meter is also suitable for availability-based tariff (ABT) regime (*see* also Annex D).

**A-1.3 Category C Meter**

This meter is identified for use at HV (PT and CT operated), LV (CT operated) consumers, 3 phase 4 wire Whole current/direct connected meter, Single phase whole current. The parameters listed for this category are for consumers who draw energy from the grid. For consumers who also supply energy to grid, the category B Meter is recommended (*see* also Annex E).

**A-2** The meters complying with this standard shall be considered as servers in a data network. The data collecting devices at the head end or HHU shall function as client and seek required services from these servers. Table 21 lists the server categories with metering nomenclatures and Annex references.

**Table 21 Categories of Meters**

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No** | **Server Category** | **Metering Nomenclature / Purpose** | **Ref to Annex**  |
| (1) | (2) | (3) | (4) |
|  |  A | Energy accounting and audit metering |  B, C, F,G |
|  |  B | Boundary / Bank / Ring / ABT metering |  B, D, F,G |
|  iv)   v) |  C1 C2  C3 | HT (PT/CT operated) and LT (CT operated) consumer meters3 Phase 4 Wire Whole current/Direct connected consumer meters

|  |
| --- |
| Single phase Whole current consumer metering |

 |      B |

NOTE**-** Annex B to Annex G are in continuation to this Annex.

|  |
| --- |
|  |

**ANNEX B**

(*Table 21*)

**INTRODUCTION TO STANDARDIZED METER PARAMETERS LIST**

**B-1 CLASSIFICATION OF PARAMETERS**

The Metering Parameters have been identified and classified as follows:

* 1. Instantaneous parameters
	2. Block profile / load survey parameters;
	3. Daily profile parameters;
	4. Parameters for accounting / billing;
	5. General purpose quantities
		1. Name Plate Details;
		2. Programmable parameters; and
	6. Event Conditions.

The measurement and computation of each of these parameters and events shall be based on standard methods or based on utilities prudent practices or as directed by respective regulatory commission.

For each of the identified parameters, the OBIS code, Interface Class and the attributes are given in the various tables in Annexure. The OBIS codes listed are applicable for LN referencing and is mandatory to adhere to by the servers and clients.

**B-2 INSTANTANEOUS PARAMETERS**

The Instantaneous parameters shall be continuously updated by the meter hardware / software as per internal sampling and computation time. The energy values in the table shall be cumulative readings from the date of manufacturing or installation of meter as the case may be. These shall be continuously updated, and the last updated value shall be available for downloading as and when required. Each of the parameters shall be readable at any instant by the HOST from remote or by HHU at site. The snapshot of all the instantaneous values of all parameters shall be readable by the HOST computer.

**B-3 PROFILE GENERIC OR LOAD SURVEY PARAMETERS (CAPTURE TIME BLOCK 15 OR 30 MIN)**

This is an array of parameters identified for capturing and storing at specified time intervals or capture times. The capture time shall be either 15 or 30 min. The capture times shall be programmable by the utilities. The tables list the parameters whose profile (survey) is to be captured and stored in the meter as per set capture time period. The profiles shall be readable at any time by the HOST from remote or by HHU (MRI) at site for any specified range and time. For the sliding window method, the sub interval period shall be 1/3rd of demand integration period.

In the case of Category B meters, the capture time shall be of 15 min. duration.

The data stored in the array shall be the average value for the captured time block and stored at the end of that block, except for energy values. The energy entries are the consumption during respective capture time block and posted at the end of that block. The array of data shall be retained inside the meter memory for the last 22 days for a capture period of 15 min. or for the last 45 days for a capture period of 30 min. It is assumed that the number of load survey parameters is 5 which can be selected from the respective tables by the utilities. The storage days can be expanded by choosing less number of parameters.

The block load profiles shall not store or return values (typically zero values) for conditions where the meter is powered down for a full day, where a full day is defined as the 24 h period from midnight 00 h to the next midnight 00 h. Under such conditions the block load profile for the entire 24 h period shall not be stored nor padded with zero entries. Whenever capture period of Block Load Survey profile is changed, the earlier load survey data shall be cleared and the load survey data with new capture period shall be available from that particular days’ first entry. However, if the meter is powered up even for a small amount of time (sufficient for it to boot up and record the Power up event) during the 24 h period, it shall store and return the block load profile for the entire 24 h duration.

**B-4 PARAMETERS FOR ACCOUNTING / BILLING PURPOSE**

These are parameters identified for accounting/billing purposes. These shall be generated by the meter for each billing cycle and stored in the memory. The set of data for the last 6 (six) cycles shall be stored in the memory. At the end of each cycle corresponding set of data shall be readable by the HOST from remote or by HHU at site.

**B-5 GENERAL PURPOSE QUANTITIES**

**B-5.1 Name Plate Details**

These parameters are electrical and non-electrical quantities and are static in nature, grouped as ‘Name Plate Details’, containing pertinent information about the supplied meter. The parameters identified and grouped as ‘Name Plate Details’ under this classification are applicable for all categories of meters (see Annex F).

**B-5.2 Programmable Parameters**

These parameters are non-electrical quantities. The parameters identified and grouped as ‘Programmable Parameters’ shall be programmable by the Utility engineers. For the purpose of setting / altering the values of these parameters, the security and access rights in line with the methodology described in protocol, shall be mutually agreed between utility and manufacturer. The parameters shall be programmable by HOST from remote and HHU at site. These are applicable for all categories of meters (see Annex F).

**B-6 EVENT CONDITIONS**

**B-6.1** Any abnormal or a tamper condition is defined as an event. The meters shall identify and log both occurrence and restoration of such events. The meters shall also capture some of the parameters at the instance of above said log. This standard has identified the events to be logged and the parameters to be captured for each of those events (see Annex G).

**B-6.2** This Companion standard has further classified those events in subgroups for easy handling. The subgroups are:

1. Voltage related events;
2. Current related events;
3. Power failure related events;
4. Transactional events;
5. Other events;
6. Non rollover events; and
7. Control events.

**B-6.3** The number of events stored in each compartment shall be decided by agreement between the Utility and Manufacturers. However, the total number of events shall be 200.

**B-6.4** The event conditions identified are listed in Table 32 to Table 38 covering all the subgroups. For each type of event condition, the parameters to be captured are listed in Table 39. The required capture parameters for selected event condition shall be chosen by the utility as per its practices and directives.

**B-6.5** The types of events to be recorded may be selected by the utility out of the list provided in tables. Table 32 to Table 38 as per Utility need and practice. The parameters for which snapshot is to be recorded at time of tamper/event can also be selected out of list of parameters provided in ‘Capture Parameters’ in Table 39.

**B-6.6** The servers shall be capable of providing the entire list of parameters listed in the respective Annexure. However, the utility as per its practices and directives may choose required parameters from the full list. The sequence of parameters in buffer shall be derived from capture object. The OBIS code for such selected parameters however shall remain as assigned.

**ANNEX C**

(*Clauses* 6.1.1 *and* A-1.1; and *Table* 21)

**PARAMETER LIST FOR CATEGORY A METERS**

**C-1** The parameters listed here are for energy accounting and audit purposes. These meters are identified for feeder metering and DTC metering where the power flow is unidirectional. In circumstances where bidirectional power flow is to be measured then Category B meters shall be deployed.

**C-2** The parameters identified are grouped under instantaneous (*see* Table 22), block load profile (*see* Table 23) and billing (*see* Table 23A). The tables include the name of the parameter, the OBIS code and Interface class.

**C-3** Association access rights are as follows:

a) *Public Client* – Read only for clock and no access for other objects.

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read and write for clock and read only for others.

**C-4 INSTANTANEOUS PARAMETERS**

Each of the parameters is a separate entity. The OBIS code for each parameter is identified as per DLMS/COSEM protocol.

**C-4.1 Snapshot of Instantaneous Parameters**

The parameters of Table 22 shall be captured as a profile generic using the country specific OBIS code 1.0.94.91.0.255; the attribute 2 of each of the capture objects shall be copied into the profile at the instant of a request from the Host.

**Table 22 Instantaneous Parameters for Category A Meters**

(*Clauses* C-2, C-4.1, C-4.2 *and* C-6)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Parameter** | **OBIS Code** | **Interface Class/Attribute** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |
| i) | Real time clock, date and time | 0 | 0 | 1 | 0 | 0 | 255 | 8/2 |
| ii) | Current, *I*R | 1 | 0 | 31 | 7 | 0 | 255 | 3/2 |
| iii) | Current, *I*Y | 1 | 0 | 51 | 7 | 0 | 255 | 3/2 |
| iv) | Current, *I*B | 1 | 0 | 71 | 7 | 0 | 255 | 3/2 |
| v) | Voltage, *V*RN | 1 | 0 | 32 | 7 | 0 | 255 | 3/2 |
| vi) | Voltage, *V*YN | 1 | 0 | 52 | 7 | 0 | 255 | 3/2 |
| vii) | Voltage, *V*BN | 1 | 0 | 72 | 7 | 0 | 255 | 3/2 |
| viii) | Voltage, *V*RY | 1 | 0 | 32 | 7 | 0 | 255 | 3/2 |
| ix) | Voltage, *V*BY | 1 | 0 | 52 | 7 | 0 | 255 | 3/2 |
| x) | Signed power factor, R-phase | 1 | 0 | 33 | 7 | 0 | 255 | 3/2 |
| xi) | Signed power factor, Y-phase | 1 | 0 | 53 | 7 | 0 | 255 | 3/2 |
| xii) | Signed power factor, B-phase | 1 | 0 | 73 | 7 | 0 | 255 | 3/2 |
| xiii) | Three phase power factor, PF | 1 | 0 | 13 | 7 | 0 | 255 | 3/2 |
| xiv) | Frequency | 1 | 0 | 14 | 7 | 0 | 255 | 3/2 |
| xv) | Apparent power, kVA | 1 | 0 | 9 | 7 | 0 | 255 | 3/2 |
| xvi) | Signed active power, kW (+ Forward; – Reverse) | 1 | 0 | 1 | 7 | 0 | 255 | 3/2 |
| xvii) | Signed reactive power, kvar (+ Lag; – Lead) | 1 | 0 | 3 | 7 | 0 | 255 | 3/2 |
| xviii) | Cumulative energy, kWh | 1 | 0 | 1 | 8 | 0 | 255 | 3/2 |
| xix) | Cumulative energy, kvarh(Lag) | 1 | 0 | 5 | 8 | 0 | 255 | 3/2 |
| xx) | Cumulative energy, kvarh (Lead) | 1 | 0 | 8 | 8 | 0 | 255 | 3/2 |
| xxi) | Cumulative energy, kVAh | 1 | 0 | 9 | 8 | 0 | 255 | 3/2 |
| xxii) | Number of power-failures. | 0 | 0 | 96 | 7 | 0 | 255 | 1/2 |
| xxiii) | Cumulative power-failure duration, min | 0 | 0 | 94 | 91 | 8 | 255 | 3/2 |
| xxiv) | Cumulative tamper count | 0 | 0 | 94 | 91 | 0 | 255 | 1/2 |
| xxv) | Cumulative billing count | 0 | 0 | 0 | 1 | 0 | 255 | 1/2 |
| xxvi) | Cumulative programmingcount | 0 | 0 | 96 | 2 | 0 | 255 | 1/2 |
| xxvii) | Billing date | 0 | 0 | 0 | 1 | 2 | 255 | 3/2 |
| xxviii) | Maximum demand, kW | 1 | 0 | 1 | 6 | 0 | 255 | 4/2, 5 |
| xxix) | Maximum demand, kVA | 1 | 0 | 9 | 6 | 0 | 255 | 4/2, 5 |

NOTES

1. The items at Sl No. (v), (vi), and (vii) are for 3φ/4W system of measurement with neutral as reference point.
2. The items at Sl No. (viii) and (ix) are for 3φ /3W system of measurement with Y-phase as reference point.
3. Signed power factor: (+) indicates lag and (–) indicates lead.
4. The parameters at Sl No. (xviii) to (xxvi) hold cumulative values at that instant from the date of manufacturing or installation of meter as the case may be.
5. The above list is identified for the purpose of communication to HOST or HHU.
6. The utilities may choose, based on needs, additional parameters for display purpose only.
7. The item number at Sl No. (xxv) refers to the billing period counter.
8. If not specified, the billing date shall be the first day of the month and the time shall be 00:00 h.
9. The parameter current *IY*  and signed power factor, Y - phase are not applicable for 3φ/3W meter.
10. The RTC — Time format by default shall be hh:mm:ss..
11. Signed power factor shall be verified at rated voltage, rated current and rated frequency at 0.5 lag and 0.8 lead.
12. Power and Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.
13. For items at Sl No. (xxviii) and (xxix) the attributes 2 and 5 of indicated IC shall be captured in instantaneous profile. The attribute 3 of indicated IC shall be captured in Scaler profile. The RTC – Time format shall be hh:mm
14. The item at Sl No. (xvi) Signed active power, kW (-Reverse), minus sign is not mandatory.
15. In case the meter is powered up with Voltage only, Sl.No. (x), (xi), (xii), (xiii) should store the value as UPF.

**C-4.2 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameters listed in Table 22. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.3.255. The capture objects for this profile shall include the scaler-unit attributes of the Instantaneous parameters listed in Table 22.

Instantaneous parameters that do not have a scaler-unit (like IC=1) shall not be included in the capture objects list. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**C-5 BLOCK LOAD PROFILE PARAMETERS**

**C-5.1** This is an array of load survey data captured as a profile generic. The OBIS code is 1.0.99.1.0.255, with Interface class as 7. The capture objects of this block load profile are as per Table 23 and the captured attribute shall be attribute 2 of each interface class. The capture object values will be copied into buffer of this array automatically as per capture period which shall be set through OBIS code 1.0.0.8.4.255 of recording interval 1.

**C-5.2** Association access rights are as follows:

a) *Public Client* – No access to all objects.

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read only for all objects.

**C-5.3 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 23. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.4.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed in Table 23. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**C-6 PARAMETERS FOR ACCOUNTING/BILLING**

The list of parameters in Table 22 and Table 23 shall be used for computing the daily accounting data at the HOST.

**Table 23 Block Load Survey Parameters for Category A Meters**

(*Clauses* C-2*,* C-5.1*,* C-5.3 *and* C-6*)*

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** |  **Parameter** | **OBIS Code****A B C D E F** | **Interface Class No. / Attribute** |
|
| 1. (1)
 | (2) | (3)(4)(5)(6)(7)(8) |  (9) |
|  | Real time clock – date and time | 0.0.1.0.0.255 |  8/2 |
|  | Current, *I*R  | 1.0.31.27.0.255 |  3/2  |
|  | Current, IY | 1.0.51.27.0.255 |  3/2 |
|  | Current, *I*B | 1.0.71.27.0.255 |  3/2 |
|  | Voltage, *V*RN | 1.0.32.27.0.255 |  3/2 |
|  | Voltage, *V*YN | 1.0.52.27.0.255 |  3/2 |
|  | Voltage, *V*BN | 1.0.72.27.0.255 |  3/2 |
|  | Voltage, VRY | 1.0.32.27.0.255 |  3/2 |
|  | Voltage, *V*BY | 1.0.52.27.0.255 |  3/2 |
| 1.
 | Block energy, in kWh | 1.0.1.29.0.255 |  3/2 |
|  | Block energy, kvarh (lag) | 1.0.5.29.0.255 |  3/2 |
|  | Block energy, in kvarh (lead) | 1.0.8.29.0.255 |  3/2 |
|  | Block energy, in kVAh | 1.0.9.29.0.255 |  3/2 |
| NOTES**1** The items at Sl No. (v), (vi), and (vii) are for 3φ /4W system of measurement with neutral as reference point.**2** The items at Sl No. (ii), (iv), Sl No. (viii) and (ix) are for 3φ/3W meter system of measurement with Y – phase as reference point.**3** The parameters at Sl No. (ii) to (ix) are the average values during the block period time and stored at the end of that time block.**4** The parameters at Sl No. (x) to (xiii) are the actual energy consumption during that time block.**5** Capture objects for 3φ/4W are items Sl No. (i) to (vii) and (x) to (xiii).**6** Capture objects for 3φ/3W meter are item Sl No. (i), (ii), (iv) and (viii) to (xiii).**7** Support for selective access shall be as defined in **11.3**.**8** The RTC — Time format by default shall be hh:mm.**9** Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead’.10 The time stamp shall be at the end of the capture period (Ist entry value is 00:15 or 00:30 minutes as applicable and last entry value is 00:00 Hrs. next day). |

**C-7 BILLING PROFILE PARAMETERS**

**C-7.1** The contents of Table 23A are for billing purpose.

**C-7.2** Association access rights are as follows:

a) *Public* Client – No access to all objects.

b) *Meter* Reader – Read only for all objects.

c) *Utility* Setting – Read only for all objects.

**Table 23A Billing Profile Parameters for Category A Meters**

 (*Clauses* C-7.1 *and C*-7.2)

|  |  |  |  |
| --- | --- | --- | --- |
| **SI No.** | **Parameter** | **OBIS Code****A B C D E F** | **Interface Class No. / Attribute** |
|
| (1) | (2) | (3) (4)(5)(6)(7)(8) | (9) |
|  | Billing date | 0.0.0.1.2.255 | 3/2 |
|  | System power factor for billing period | 1.0.13.0.0.255 | 3/2 |
|  | Cumulative energy, kWh | 1.0.1.8.0.255 | 3/2 |
|  | Cumulative energy, kWh for TZ1 | 1.0.1.8.1.255 | 3/2 |
|  | Cumulative energy, kWh for TZ2 | 1.0.1.8.2.255 | 3/2 |
|  | Cumulative energy, kWh for TZ3 | 1.0.1.8.3.255 | 3/2 |
|  | Cumulative energy, kWh for TZ4 | 1.0.1.8.4.255 | 3/2 |
|  | Cumulative energy, kWh for TZ5 | 1.0.1.8.5.255 | 3/2 |
|  | Cumulative energy, kWh for TZ6 | 1.0.1.8.6.255 | 3/2 |
|  | Cumulative energy, kWh for TZ7 | 1.0.1.8.7.255 | 3/2 |
|  | Cumulative energy, kWh for TZ8 | 1.0.1.8.8.255 | 3/2 |
|  | Cumulative energy, kvarh (Lag) | 1.0.5.8.0.255 | 3/2 |
|  | Cumulative energy, kvarh (Lead) | 1.0.8.8.0.255 | 3/2 |
|  | Cumulative energy, kVAh | 1.0.9.8.0.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ1 | 1.0.9.8.1.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ2 | 1.0.9.8.2.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ3 | 1.0.9.8.3.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ4 | 1.0.9.8.4.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ5 | 1.0.9.8.5.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ6 | 1.0.9.8.6.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ7 | 1.0.9.8.7.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ8 | 1.0.9.8.8.255 | 3/2 |
|  | MD, kW | 1.0.1.6.0.255 | 4/2 ,5 |
|  | MD, kW for TZ1 | 1.0.1.6.1.255 | 4/2 ,5 |
|  | MD, kW for TZ2 | 1.0.1.6.2.255 | 4/2 ,5 |
|  | MD, kW for TZ3 | 1.0.1.6.3.255 | 4/2 ,5 |
|  | MD, kW for TZ4 | 1.0.1.6.4.255 | 4/2 ,5 |
|  | MD, kW for TZ5 | 1.0.1.6.5.255 | 4/2 ,5 |
|  | MD, kW for TZ6 | 1.0.1.6.6.255 | 4/2 ,5 |
|  | MD, kW for TZ7 | 1.0.1.6.7.255 | 4/2 ,5 |
|  | MD, kW for TZ8 | 1.0.1.6.8.255 | 4/2 ,5 |
|  | MD, kVA | 1.0.9.6.0.255 | 4/2 ,5 |
|  | MD, kVA for TZ1 | 1.0.9.6.1.255 | 4/2 ,5 |
|  | MD, kVA for TZ2 | 1.0.9.6.2.255 | 4/2 ,5 |
|  | MD, kVA for TZ3 | 1.0.9.6.3.255 | 4/2 ,5 |
|  | MD, kVA for TZ4 | 1.0.9.6.4.255 | 4/2 ,5 |
|  | MD, kVA for TZ5 | 1.0.9.6.5.255 | 4/2 ,5 |
|  | MD, kVA for TZ6 | 1.0.9.6.6.255 | 4/2 ,5 |
|  | MD, kVA for TZ7 | 1.0.9.6.7.255 | 4/2 ,5 |
|  | MD, kVA for TZ8 | 1.0.9.6.8.255 | 4/2 ,5 |
|  | Billing Power ON duration in Minutes | 0.0.94.91.13.255 | 3/2 |
| NOTES**1** The data is stored up to 6 billing cycles. The billing profile is modeled as Profile generic (IC = 7) object with OBIS Code 1.0.98.1.0.255. The capture objects of this load profile are as per Table 29. The capture object values will be copied into buffer of this object either automatically or asynchronously. The capture period is set to zero, billing action is controlled by billing dates as provided in 10 and Table 31.**2** Support for selective access shall be as defined in **11.3**.**3** The current cycle billing parameters shall be readable as the values of the latest billing period, on demand. This shall be in addition to the last 6 billing period data which shall be available in the profile buffer as the last 6 entries in the buffer.**4** The captured attributes in the case of Interface Class 4 (Extended register) used for MD values will be attributes 2 and 5 (Value and Timestamp).**5** The RTC — Time format by default shall be hh:mm.’. **6** Billing date and time shall be current date and current time. |

**ANNEX D**

(*Clauses* 6.1.1 *and* A-1.2; and *Table* 21)

## PARAMETER LIST FOR CATEGORY B METERS

**D-1** The parameters listed here are for Boundary/Bank/Ring Fencing /ABT Metering. The meter records parameters under import and or export conditions.

**D-2** The parameters identified for this are grouped under instantaneous (*see* Table 24), block load profile (*see* Table 25), daily load profile (*see* Table 26) and billing (*see* Table 56). The tables include the name of the parameter, the OBIS code and interface class.

**D-3 INSTANTANEOUS PARAMETERS**

**D-3.1** Each of the parameters is a separate entity. The OBIS code for each parameter is identified as per DLMS /COSEM protocol.

**D-3.2** Association access rights are as follows:

a) *Public Client* – Read only for clock and no access for other objects.

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read & write for clock and read only for others.

**D-3.3 Snapshot of Instantaneous Parameters**

The parameters of Table 24 shall be captured as a profile generic using the country specific OBIS code 1.0.94.91.0.255. The attribute 2 of each of the capture objects shall be copied into the profile at the instant of a request from the Host.

**Table 24 Instantaneous Parameters for Category B Meters**

(*Clauses*D-2, D-3.3 *and* D-3.4)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Parameter** | **OBIS Code** | **Interface Class/Attribute** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |
| i) | Real time clock, date and time | 0 | 0 | 1 | 0 | 0 | 255 | 8/2 |
| ii) | Current, *I*R | 1 | 0 | 31 | 7 | 0 | 255 | 3/2 |
| iii) | Current, *I*Y | 1 | 0 | 51 | 7 | 0 | 255 | 3/2 |
| iv) | Current, *I*B | 1 | 0 | 71 | 7 | 0 | 255 | 3/2 |
| v) | Voltage, *V*RN | 1 | 0 | 32 | 7 | 0 | 255 | 3/2 |
| vi) | Voltage, *V*YN | 1 | 0 | 52 | 7 | 0 | 255 | 3/2 |
| vii) | Voltage, *V*BN | 1 | 0 | 72 | 7 | 0 | 255 | 3/2 |
| viii) | Voltage, *V*RY | 1 | 0 | 32 | 7 | 0 | 255 | 3/2 |
| ix) | Voltage, *V*BY | 1 | 0 | 52 | 7 | 0 | 255 | 3/2 |
| x) | Signed power factor, R-phase | 1 | 0 | 33 | 7 | 0 | 255 | 3/2 |
| xi) | Signed power factor, Y-phase | 1 | 0 | 53 | 7 | 0 | 255 | 3/2 |
| xii) | Signed power factor, B-phase | 1 | 0 | 73 | 7 | 0 | 255 | 3/2 |
| xiii) | Three phase power factor, PF | 1 | 0 | 13 | 7 | 0 | 255 | 3/2 |
| xiv) | Frequency | 1 | 0 | 14 | 7 | 0 | 255 | 3/2 |
| xv) | Apparent power, kVA | 1 | 0 | 9 | 7 | 0 | 255 | 3/2 |
| xvi) | Signed active power, kW (+ import: **–** export) | 1 | 0 | 1 | 7 | 0 | 255 | 3/2 |
| xvii) | Signed reactive power, kvar (+ Lag; **–** Lead) | 1 | 0 | 3 | 7 | 0 | 255 | 3/2 |
| xviii) | Cumulative energy, kWh (Import) | 1 | 0 | 1 | 8 | 0 | 255 | 3/2 |
| xix) | Cumulative energy, kWh (Export) | 1 | 0 | 2 | 8 | 0 | 255 | 3/2 |
| xx) | Cumulative energy, kVAh (Import) | 1 | 0 | 9 | 8 | 0 | 255 | 3/2 |
| xxi) | Cumulative energy, kVAh (Export) | 1 | 0 | 10 | 8 | 0 | 255 | 3/2 |
| xxii) | Number of power, failures. | 0 | 0 | 96 | 7 | 0 | 255 | 1/2 |
| xxiii) | Cumulative power failure duration,min | 0 | 0 | 94 | 91 | 8 | 255 | 3/2 |
| xxiv) | Cumulative tamper count | 0 | 0 | 94 | 91 | 0 | 255 | 1/2 |
| xxv) | Cumulative billing count | 0 | 0 | 0 | 1 | 0 | 255 | 1/2 |
| xxvi) | Cumulative programming count | 0 | 0 | 96 | 2 | 0 | 255 | 1/2 |
| xxvii) | Billing date | 0 | 0 | 0 | 1 | 2 | 255 | 3/2 |

NOTES

1. The items at Sl No. (v), (vi) and (vii) are for 3φ/4W system of measurement with neutral as reference point.
2. The items at Sl No. (viii), (ix) are for 3φ /3W system of measurement with Y-phase as reference point.
3. Signed Power factor: (+) indicates lag and (–) indicates lead.
4. The parameters at Sl No. (xviii) to (xxvi) hold cumulative values at that instant from the date of manufacturing or installation of meter as the case may be.
5. The above list is identified for the purpose of communication to HOST or HHU.
6. The utilities may choose, based on needs, additional parameters for display purpose only.
7. Item number at Sl No. (xxv) refers to the billing period counter.
8. If not specified, the billing date shall be first day of the month and time shall be 00:00 h.
9. The parameters current *I*Y and signed power factor, Y – phase are not applicable for 3φ/ 3W meter.
10. The RTC — Time format by default shall be hh:mm:ss
11. Signed power factor shall be verified at rated voltage, rated current and rated frequency at 0.5 lag and 0.8 lead.
12. Power and Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.

 **13** In case meter is powered up with Voltage only, Sl.No. (x), (xi), (xii) and (xiii) should store the value as UPF.

**D-3.4 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 24. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.3.255. The capture objects for this profile shall include the scaler-unit attributes of the Instantaneous parameters listed in Table 24. Instantaneous parameters that do not have a scaler-unit (like IC=1) shall not be included in the capture objects list. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**D-4 BLOCK LOAD PROFILE PARAMETERS**

**D 4.1** This is an array of load survey data captured as a profile generic. The OBIS code is 1.0.99.1.0.255, with Interface class as 7. The capture objects of this block load profile are as per Table 25 and the captured object shall be attribute 2 of each interface class. The capture object values will be copied into a buffer of this array automatically as per capture period which shall be set through OBIS code 1.0.0.8.4.255 of recording interval 1.

**D 4.2** Association access rights are as follows:

a) *Public Client* – No access for all objects

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read only for all objects.

**Table 25 Block Load Survey Parameters for Category B Meters**

(*Clauses* D-2 and D-4.3)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Parameter** | **OBIS Code****A B C D E F** | **Interface Class No. / Attribute** |
|
| (1) | (2) | (3) (4)(5)(6)(7)(8) | (9) |
|  | Real Time Clock, date and time | 0.0.1.0.0.255 | 8 / 2 |
|  | Frequency | 1.0.14.27.0.255 | 3 / 2 |
|  | Voltage, *V*RN/*V*RY  | 1.0.32.27.0.255 | 3 / 2 |
|  | Voltage, *V*YN/*V*YB  | 1.0.52.27.0.255 | 3 / 2 |
|  | Voltage, *V*BN/*V*BR  | 1.0.72.27.0.255 | 3 / 2 |
|  | Energy – active import | 1.0.1.29.0.255 | 3 / 2 |
|  | Energy – net active energy | 1.0.16.29.0.255 | 3 / 2 |
|  | Energy – active export | 1.0.2.29.0.255 | 3 / 2 |
|  | Energy, kvarh, Quadrant I | 1.0.5.29.0.255 | 3 / 2 |
|  | Energy, kvarh, Quadrant II | 1.0.6.29.0.255 | 3 / 2 |
|  | Energy, kvarh, Quadrant III | 1.0.7.29.0.255 | 3 / 2 |
|  | Energy, kvarh, Quadrant IV | 1.0.8.29.0.255 | 3 / 2 |
| NOTES**1** The parameters listed in this table are for load survey purpose and are logged as per the block period time.**2** The block period time for interface meters is fixed at 15 min for which the data storage will be for 22 days.**3** The parameters at Sl No. (iii) to (vi) are the average values of 15 min block and stored at the end of that time block.**4** The parameters at Sl No. (vii) to (xii) are the actual energy consumption during the 15 min time block.**5** Item at Sl No. (ii) is an ABT parameter for absolute average value.**6** Item at Sl No. (vii) is an ABT parameter for net energy in the current 15 min block.**7** Support for selective access shall be as defined in **11.3**.**8** The RTC — Time format by default shall be hh:mm.**9** *V*RN, *V*YN and *V*BN are for 3φ/4W meter and VRY and VBY are for 3φ/3W meter.**10** Active Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.’**11** The time stamp shall be at the end of the capture period (Ist entry value is 00:15 or 00:30 minutes as applicable and last entry value is 00:00 Hrs. next day)’. |

**D-4.3 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 25. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.4.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed in Table 25. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**D-5 DAILY LOAD PROFILE PARAMETERS**

**D-5.1** This is an array of load survey data captured as a profile generic at the end of 24 h. The OBIS code is 1.0.99.2.0.255, with Interface class as 7. The capture objects of this daily load profile are as per Table 26 and the captured attribute shall be attribute 2 of each interface class. The capture object values will be copied into a buffer of this array automatically as per capture period which shall be statically fixed as 24 h.

**D-5.2** Association access rights are as follows:

a) *Public Client* – No access for all objects

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read only for all objects.

**Table 26 Daily Load Profile Parameters for Category B Meters**

(*Clauses* D-2 *and* D-5.1*)*

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Parameter** | **OBIS Code****A B C D E F** |  **Interface Class No. / Attribute** |
|
| (1) | (2) | (3) (4)(5)(6)(7)(8) | (9) |
|  | Real time clock, date and time | 0.0.1.0.0.255 | 8 / 2 |
|  | Cumulative energy, kWh (Import) | 1.0.1.8.0.255 | 3 / 2 |
|  | Cumulative energy, kWh (Export) | 1.0.2.8.0.255 | 3 / 2 |
|  | Cumulative energy, kVAh while kW Import | 1.0.9.8.0.255 | 3 / 2 |
|  | Cumulative energy, kVAh while kW Export | 1.0.10.8.0.255 | 3 / 2 |
|  | Reactive energy high (V > 103 percent) | 1.0.94.91.1.255 | 3 / 2 |
|  | Reactive energy low (V < 97 percent) | 1.0.94.91.2.255 | 3 / 2 |
|  | Cumulative energy, kvarh, Quadrant 1 | 1.0.5.8.0.255 | 3 / 2 |
|  | Cumulative energy, kvarh, Quadrant 2 | 1.0.6.8.0.255 | 3 / 2 |
|  | Cumulative energy, kvarh , Quadrant 3 | 1.0.7.8.0.255 | 3 / 2 |
|  | Cumulative energy, kvarh , Quadrant 4 | 1.0.8.8.0.255 | 3 / 2 |
| NOTES**1** The parameters listed in this table are meant for billing purpose and shall be logged at midnight (00 h).**2** The storage time for these parameters is 22 days.**3** The parameters at Sl No. (ii) to (xi) are cumulative values at that instant from the date of manufacturing or installation of meter as the case may be.**4** Item at Sl No. (vi) is an ABT parameter.**5** Item at Sl No. (vii) is an ABT parameter.**6** Support for selective access shall be as defined in **11.3**.**7** The RTC — Time format by default shall be hh:mm. **8** Power and Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.  |

**D-5.3 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 26. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.5.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed in table 26. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**D-6 BILLING PROFILE PARAMETERS**

**D-6.1** The billing profile parameters for category B meters are listed in Table 56.

**D-6.2** Association access rights are as follows:

a) *Public* Client – No access to all objects.

b) *Meter* Reader – Read only for all objects.

c) *Utility* Setting – Read only for all objects.

**Table 56 Billing Profile Parameters for category B meters**

(***Clause* D-6.1, D-6.2)**

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Parameter** | **OBIS Code** | **Interface Class No. /Attribute** |
|  |  | A | B | C | D | E | F |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |
| i)  | Billing date  | 0  | 0  | 0  | 1  | 2  | 255  | 3/2  |
| ii)  | Cumulative energy, kWh (Import)  | 1  | 0  | 1  | 8  | 0  | 255  | 3/2  |
| iii)  | Cumulative energy, kWh (Export)  | 1  | 0  | 2  | 8  | 0  | 255  | 3/2  |
| iv)  | Cumulative energy, kVAh (Import)  | 1  | 0  | 9  | 8  | 0  | 255  | 3/2  |
| v)  | Cumulative energy, kVAh (Export)  | 1  | 0  | 10  | 8  | 0  | 255  | 3/2  |
| vi)  | Cumulative energy, kvarh, Quadrant I  | 1  | 0  | 5  | 8  | 0  | 255  | 3/2  |
| vii)  | Cumulative energy, kvarh, Quadrant II  | 1  | 0  | 6  | 8  | 0  | 255  | 3/2  |
| viii)  | Cumulative energy, kvarh, Quadrant III  | 1  | 0  | 7  | 8  | 0  | 255  | 3/2  |
| ix)  | Cumulative energy, kvarh, Quadrant IV  | 1  | 0  | 8  | 8  | 0  | 255  | 3/2  |
| x)  | Power ON duration in minutes  | 0  | 0  | 94  | 91  | 13  | 255  | 3/2  |

NOTES

**1** The data is stored up to 6 billing cycles. The billing profile is modeled as Profile generic (IC = 7) object with OBIS Code 1.0.98.1.0.255. The capture objects of this load profile are as per Table. The capture object values will be copied into buffer of this object either automatically or asynchronously. The capture period is set to zero; billing action is controlled by billing dates as provided in cl. 10 and Table 31.

**2** Support for selective access shall be as defined in 1**1.3**.

**3** The current cycle billing parameters shall be readable as the values of the latest billing period, on demand. This shall be in addition to the last 6 billing period data which shall be available in the profile buffer as the last 6 entries in the buffer.

**4** The Billing Date - Time format by default shall be HH:MM.

5 Billing Date and Time shall be current date and current time.

**ANNEX E**

(*Clauses* 6.11 *and* A-1.3*; and Table* 21*)*

## PARAMETER LIST FOR CATEGORY C METERS

**E-1** The parameters listed here are for HV (VT/CT), LV (CT) consumer metering,

3 phase 4 wire whole current/direct connected meter. This meter records energy in import mode. These meters shall be capable of recording Import of energy. For customers who import energy and also export energy, use of category B meters is recommended. Category A meter shall be considered as subset of Category C meter. The meter complying for Category C shall be deemed as complying to Category A also.

**E-2** The parameters identified for this are grouped under instantaneous (*see* Table 27), block load profile (*see* Table 28), and billing (*see* Table 29). The tables include the name of the parameter, the OBIS code and interface class.

**E-3 INSTANTANEOUS PARAMETERS**

**E-3.1** Each of the parameters is a separate entity. The OBIS code for each parameter is identified as per DLMS/COSEM protocol.

Association access rights are as follows:

a) *Public client* – Read only for clock and no access for other objects.

b) *Meter reader* – Read only for all objects.

c) *Utility setting* – Read and write for clock and read only for others.

**E-3.2 Snapshot of Instantaneous Parameters**

The parameters of Table 27 shall be captured as a profile generic using the country specific OBIS code 1.0.94.91.0.255. The attribute 2 of each of the capture objects shall be copied into the profile at the instant of a request from the Host.

**Table 27 Instantaneous Parameters for Category C Meters**

(*Clauses*E-2, E-3.2 *and* E-3.3)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl no.** | **Parameter** | **OBIS Code** | **Interface Class/Attribute** |
| **A** | **B** | **C** | **D** | **E** | **F** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |  (9) |
| i) | Real time clock, date and time | 0 | 0 | 1 | 0 | 0 | 255 | 8/2 |
| ii) | Current, *I*R | 1 | 0 | 31 | 7 | 0 | 255 | 3/2 |
| iii) | Current, *I*Y | 1 | 0 | 51 | 7 | 0 | 255 | 3/2 |
| iv) | Current, *I*B | 1 | 0 | 71 | 7 | 0 | 255 | 3/2 |
| v) | Voltage, *V*RN | 1 | 0 | 32 | 7 | 0 | 255 | 3/2 |
| vi) | Voltage, *V*YN | 1 | 0 | 52 | 7 | 0 | 255 | 3/2 |
| vii) | Voltage, *V*BN | 1 | 0 | 72 | 7 | 0 | 255 | 3/2 |
| viii) | Voltage, *V*RY | 1 | 0 | 32 | 7 | 0 | 255 | 3/2 |
| ix) | Voltage, *V*BY | 1 | 0 | 52 | 7 | 0 | 255 | 3/2 |
| x) | Signed power factor, *R*-phase | 1 | 0 | 33 | 7 | 0 | 255 | 3/2 |
| xi) | Signed power factor, *Y*-phase | 1 | 0 | 53 | 7 | 0 | 255 | 3/2 |
| xii) | Signed power factor, *B*-phase | 1 | 0 | 73 | 7 | 0 | 255 | 3/2 |
| xiii) | Three phase power factor, PF | 1 | 0 | 13 | 7 | 0 | 255 | 3/2 |
| xiv) | Frequency | 1 | 0 | 14 | 7 | 0 | 255 | 3/2 |
| xv) | Apparent power, kVA | 1 | 0 | 9 | 7 | 0 | 255 | 3/2 |
| xvi) | Signed active power, kW (+ Forward; **–** Reverse) | 1 | 0 | 1 | 7 | 0 | 255 | 3/2 |
| xvii) | Signed reactive power, kvar (+ Lag; **–** Lead) | 1 | 0 | 3 | 7 | 0 | 255 | 3/2 |
| xviii) | Number of powers **—** failures | 0 | 0 | 96 | 7 | 0 | 255 | 1/2 |
| xix) | Cumulative power failure duration,min | 0 | 0 | 94 | 91 | 8 | 255 | 3/2 |
| xx) | Cumulative tamper count | 0 | 0 | 94 | 91 | 0 | 255 | 1/2 |
| xxi) | Cumulative billing count | 0 | 0 | 0 | 1 | 0 | 255 | 1/2 |
| xxii) | Cumulative programming count | 0 | 0 | 96 | 2 | 0 | 255 | 1/2 |
| xxiii) | Billing date | 0 | 0 | 0 | 1 | 2 | 255 | 3/2 |
| xxiv) | Cumulative energy, kWh | 1 | 0 | 1 | 8 | 0 | 255 | 3/2 |
| xxv) | Cumulative energy, kvarh (Lag) | 1 | 0 | 5 | 8 | 0 | 255 | 3/2 |
| xxvi) | Cumulative energy, kvarh (Lead) | 1 | 0 | 8 | 8 | 0 | 255 | 3/2 |
| xxvii) | Cumulative energy, kVAh | 1 | 0 | 9 | 8 | 0 | 255 | 3/2 |
| xxviii) | Maximum Demand, kW | 1 | 0 | 1 | 6 | 0 | 255 | 4/2,5 |
| xxix) | Maximum Demand, kVA | 1 | 0 | 9 | 6 | 0 | 255 | 4/2,5 |

NOTES

1. The items at Sl No. (v), (vi) and (vii) are for 3φ /4W system of measurement with NEUTRAL as reference point.
2. The items at Sl No. (viii) and (ix) are for 3φ /3W system of measurement with Y-Phase as reference point.
3. Signed Power factor: (+) indicates lag and (–) indicates lead.
4. The parameters at Sl No. (xviii) to (xxii) hold cumulative values at that instant from the date of manufacturing or installation of meter as the case may be.
5. The above list is identified for the purpose of communication to HOST or HHU.
6. The utilities may choose, based on needs, additional parameters for display purpose only.
7. Item at Sl No. (xxi) refers to the Billing Period Counter.
8. Item at Sl No. (xxiii) **—** Data type to be same as for attribute 2 of IC = 8, Clock. If not specified, the billing date shall be first day of the month and time shall be 00:00 h.’
9. The item at Sl No. (xvi) Signed active power, kW (-Reverse), minus sign is not mandatory.

**10** The parameter Current *I*Y and Signed power factor, Y- phase are not applicable for 3φ/ 3W meter.

 **11** The RTC — Time format by default shall be hh:mm:ss.

 **12** Signed power factor shall be verified at rated voltage, rated current and rated frequency at 0.5 lag and 0.8 lead.

 **13** Power and Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.

**14** For Sl No. (xxviii) and (xxix), the attributes 2 and 5 of indicated IC shall be captured in instantaneous profile. The attribute 3 of indicated IC shall be captured in Scaler profile. The RTC — Time format shall be HH:MM.

 **15** In case meter is powered up with Voltage only, Sl.No. (x), (xi), (xii) and (xiii) should store the value as UPF.

**E-3.3 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 27. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.3.255. The capture objects for this profile shall include the scaler-unit attributes of the instantaneous parameters listed in Table 27 instantaneous parameters that do not have a scaler-unit (like IC=1) shall not be included in the capture objects list. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**E-4 BLOCK LOAD PROFILE PARAMETERS**

**E-4.1** This is an array of load survey data captured as a profile generic. The OBIS code is 1.0.99.1.0.255, with Interface class as 7. The capture objects of this block load profile are as per Table 28 and the captured attribute shall be 2 of each interface class. The capture object values will be copied into a buffer of this array automatically as per capture period which shall be set through OBIS code 1.0.0.8.4.255 of recording interval 1.

**E-4.2** Association access rights are as follows:

a) *Public Client* – No access to all objects.

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read only for all objects.

**Table 28 Block Load Survey Parameters for Category C Meters**

(*Clauses* E-2*,* E-4.1 *and* E-4.3*)*

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Parameter** | **OBIS Code****A B C D E F** | **Interface Class No. / Attribute** |
|
| (1) | (2) | (3) (4)(5)(6)(7)(8) | (9) |
|  | Real time clock, date and time | 0.0.1.0.0.255 | 8/2 |
|  | Current, *I*R  | 1.0.31.27.0.255 | 3/2 |
|  | Current, *I*Y | 1.0.51.27.0.255 | 3/2 |
|  | Current, *I*B | 1.0.71.27.0.255 | 3/2 |
|  | Voltage, *V*RN | 1.0.32.27.0.255 | 3/2 |
|  | Voltage, *V*YN | 1.0.52.27.0.255 | 3/2 |
|  | Voltage, *V*BN | 1.0.72.27.0.255 | 3/2 |
|  | Voltage, *V*RY | 1.0.32.27.0.255 | 3/2 |
|  | Voltage, *V*BY | 1.0.52.27.0.255 | 3/2 |
|  | Block energy, kWh | 1.0.1.29.0.255 | 3/2 |
|  | Block energy, kvarh (lag) | 1.0.5.29.0.255 | 3/2 |
|  | Block energy, kvarh (lead) | 1.0.8.29.0.255 | 3/2 |
|  | Block energy, kVAh | 1.0.9.29.0.255 | 3/2 |
| NOTES**1** The parameters listed in this table are for load survey purpose and are logged as per the block period time.**2** The parameters at Sl No. (ii) to (ix) are the average values during the block period time and stored at the end of that time block.**3** The parameters at Sl No. (x) to (xiii) are the actual energy consumption during that time block.**4** Capture objects for 3φ/4W are items at Sl No. (i) to (vii) and (x) to (xiii).**5**Capture objects for 3 φ /3W meter are items at Sl. No. (i), (ii), (iv) and (viii) to (xiii).**6** Support for selective access shall be as defined in **11.3**.**7** The parameter current *I*Y is not applicable for 3φ/ 3W meter.**8** The RTC-time format by default shall be hh:mm.**9** Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.10 The time stamp shall be at the end of the capture period (Ist entry value is 00:15 or 00:30 minutes as applicable and last entry value is 00:00 Hrs. next day).  |

**E-4.3 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 28. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.4.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed in Table 28. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**E-5 BILLING PROFILE PARAMETERS**

**E-5.1** The contents of Table 29 are for billing purpose. The billing profile parameters is also applicable for category A meters. The billing profile parameters for category B meters are listed in Table 56

**E-5.2** Association access rights are as follows:

a) *Public* Client – No access to all objects.

b) *Meter* Reader – Read only for all objects.

c) *Utility* Setting – Read only for all objects.

**Table 29 Billing Profile Parameters for Category C Meters**

 (*Clauses* E-5.1 *and E*-5.3)

|  |  |  |  |
| --- | --- | --- | --- |
| **SI No.** | **Parameter** | **OBIS Code****A B C D E F** | **Interface Class No. / Attribute** |
|
| (1) | (2) | (3) (4)(5)(6)(7)(8) | (9) |
|  | Billing date | 0.0.0.1.2.255 | 3/2 |
|  | System power factor for billing period | 1.0.13.0.0.255 | 3/2 |
|  | Cumulative energy, kWh | 1.0.1.8.0.255 | 3/2 |
|  | Cumulative energy, kWh for TZ1 | 1.0.1.8.1.255 | 3/2 |
|  | Cumulative energy, kWh for TZ2 | 1.0.1.8.2.255 | 3/2 |
|  | Cumulative energy, kWh for TZ3 | 1.0.1.8.3.255 | 3/2 |
|  | Cumulative energy, kWh for TZ4 | 1.0.1.8.4.255 | 3/2 |
|  | Cumulative energy, kWh for TZ5 | 1.0.1.8.5.255 | 3/2 |
|  | Cumulative energy, kWh for TZ6 | 1.0.1.8.6.255 | 3/2 |
|  | Cumulative energy, kWh for TZ7 | 1.0.1.8.7.255 | 3/2 |
|  | Cumulative energy, kWh for TZ8 | 1.0.1.8.8.255 | 3/2 |
|  | Cumulative energy, kvarh (Lag) | 1.0.5.8.0.255 | 3/2 |
|  | Cumulative energy, kvarh (Lead) | 1.0.8.8.0.255 | 3/2 |
|  | Cumulative energy, kVAh | 1.0.9.8.0.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ1 | 1.0.9.8.1.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ2 | 1.0.9.8.2.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ3 | 1.0.9.8.3.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ4 | 1.0.9.8.4.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ5 | 1.0.9.8.5.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ6 | 1.0.9.8.6.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ7 | 1.0.9.8.7.255 | 3/2 |
|  | Cumulative energy, kVAh for TZ8 | 1.0.9.8.8.255 | 3/2 |
|  | MD, kW | 1.0.1.6.0.255 | 4/2 ,5 |
|  | MD, kW for TZ1 | 1.0.1.6.1.255 | 4/2 ,5 |
|  | MD, kW for TZ2 | 1.0.1.6.2.255 | 4/2 ,5 |
|  | MD, kW for TZ3 | 1.0.1.6.3.255 | 4/2 ,5 |
|  | MD, kW for TZ4 | 1.0.1.6.4.255 | 4/2 ,5 |
|  | MD, kW for TZ5 | 1.0.1.6.5.255 | 4/2 ,5 |
|  | MD, kW for TZ6 | 1.0.1.6.6.255 | 4/2 ,5 |
|  | MD, kW for TZ7 | 1.0.1.6.7.255 | 4/2 ,5 |
|  | MD, kW for TZ8 | 1.0.1.6.8.255 | 4/2 ,5 |
|  | MD, kVA | 1.0.9.6.0.255 | 4/2 ,5 |
|  | MD, kVA for TZ1 | 1.0.9.6.1.255 | 4/2 ,5 |
|  | MD, kVA for TZ2 | 1.0.9.6.2.255 | 4/2 ,5 |
|  | MD, kVA for TZ3 | 1.0.9.6.3.255 | 4/2 ,5 |
|  | MD, kVA for TZ4 | 1.0.9.6.4.255 | 4/2 ,5 |
|  | MD, kVA for TZ5 | 1.0.9.6.5.255 | 4/2 ,5 |
|  | MD, kVA for TZ6 | 1.0.9.6.6.255 | 4/2 ,5 |
|  | MD, kVA for TZ7 | 1.0.9.6.7.255 | 4/2 ,5 |
|  | MD, kVA for TZ8 | 1.0.9.6.8.255 | 4/2 ,5 |
|  | Billing Power ON duration in Minutes | 0.0.94.91.13.255 | 3/2 |
|  ~~xli) Total power ON duration in minutes 0.0.94.91.13.255 3~~ ~~with ‘Billing Power ON duration in Minutes (During billing period)~~NOTES**1** The data is stored up to 6 billing cycles. The billing profile is modeled as Profile generic (IC = 7) object with OBIS Code 1.0.98.1.0.255. The capture objects of this load profile are as per Table 29. The capture object values will be copied into buffer of this object either automatically or asynchronously. The capture period is set to zero, billing action is controlled by billing dates as provided in 10 and Table 31.**2** Support for selective access shall be as defined in **11.3**.**3** The current cycle billing parameters shall be readable as the values of the latest billing period, on demand. This shall be in addition to the last 6 billing period data which shall be available in the profile buffer as the last 6 entries in the buffer.**4** The captured attributes in the case of Interface Class 4 (Extended register) used for MD values will be attributes 2 and 5 (Value and Timestamp).**5** The RTC — Time format by default shall be hh:mm.’. **6** Billing date and time shall be current date and current time. |

**E-5.3 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 29. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.6.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed in Table 29. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**E-12- DAILY LOAD PROFILE PARAMETERS**

This is an array of load survey data captured as a profile generic at the end of 24 h. The OBIS code is 1.0.99.2.0.255 with IC as 7. The capture objects of this daily load profile are as per Table 57 and the captured attribute shall be 2 of each Interface class. The capture object values will be copied into a buffer of this array automatically as per capture period which shall be statically fixed as 24 h.

Association access rights are as follows:

 a) *Public client* — No access to all objects.

 b) *Meter reader* — Read only for all objects.

 c) *Utility setting* — Read only for all objects.

**Table 57 Daily Load profile parameters**

(*Clause* **E-12** and **E-12.1**)

|  |  |  |  |
| --- | --- | --- | --- |
| Sl No. | **Parameter** | **OBIS Code** | **Interface Class/Attribute** |
|  |  | A | B | C | D | E | F |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |
| i) | Real time clock, date and time | 0 | 0 | 1 | 0 | 0 | 255 | 8/2 |
| ii) | Cumulative energy, kWh | 1 | 0 | 1 | 8 | 0 | 255 | 3/2 |
| iii) | Cumulative energy, kVAh | 1 | 0 | 9 | 8 | 0 | 255 | 3/2 |
| NOTES: **1** The parameters listed in this table are meant for billing purpose and shall be logged at midnight (00 h). **2** The storage time for these parameters is the same as Block load survey. **3** Support for selective access shall be as defined in **11.3**  |  |

**E-12.1 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 57. This is modeled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.5.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed in Table 57. The profile buffer shall have only one entry.

This profile is not required to be updated periodically.

**E-6 LIST OF PARAMETERS FOR CATEGORY C3 METER (SINGLE PHASE WHOLE CURRENT METER)**

The parameters listed are for single phase whole current consumer metering. This meter records energy in import mode. These meters shall be capable of recording the import of energy.

The parameters identified for this are grouped under instantaneous parameters (*see* Table 43), block load profile (*see* Table 44), daily load profile (*see* Table 45), billing profile (*see* Table 46), name plate details (*see* Table 47), programmable parameters (*see* Table 48) and Indian reference tables (*see* Tables 49 to 54).

**E-6.1 Instantaneous Parameters**

Each of the parameters is a separate entity. The OBIS code for each parameter is identified as per DLMS/COSEM protocol.

 Association access rights are as follows:

 a) *Public client* **—** Read only for clock and no access for other objects.

 b) *Meter reader* — Read only for all objects.

 c) *Utility setting* — Read only for all objects.

 The instantaneous parameters are listed in Table 43.

 **E-6.2 Snapshot of Instantaneous Parameters**

 The parameters of Table 43 shall be captured as a profile generic using the country specific OBIS code 1.0.94.91.0.255. The attribute 2 of each of the captured objects shall be copied into the profile at the instant of a request from the HOST.

 **E-6.3 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 43. This is modelled as profile generic (IC = 7) and is assigned the country specific OBIS code 1.0.94.91.3.255. The capture objects for this profile shall include the scaler unit attributes of the instantaneous parameters listed in Table 43. Instantaneous parameters that do not have a scaler-unit (like IC = 1) shall not be included in the capture objects list. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**E-7 BLOCK LOAD PROFILE PARAMETERS**

This is an array of load survey data captured as a profile. The OBIS code is 1.0.99.1.0.255, with Interface class as 7. The capture objects of this block load profile are listed in Table 44 and the captured attribute shall be 2 of each interface class. The capture object values shall be copied into a buffer of this array automatically as per capture period which shall be set through OBIS code 1.0.0.8.4.255 of recording interval 1. The array of data shall be retained inside the meter memory for the last 35.

days for a capture period of 1800 seconds for maximum of 4 parameters including real time clock-date and time.

Association access rights are as follows:

 a) *Public client* — No access to all objects.

 b) *Meter reader* — Read only for all objects.

 c) *Utility setting* — Read only for all objects.

**E-7.1 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 44. This is modelled as profile generic (IC = 7) and is assigned the country specific OBIS code 1.0.94.91.4.255. The capture objects for this profile shall include the scaler unit attributes (column 4) of the parameters listed in Table 44 and parameters that do not have a scaler-unit (like IC = 1) shall not be included in the capture objects list. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**E-8 DAILY LOAD PROFILE PARAMETERS**

This is an array of load survey data captured as a profile generic at the end of 24 h. The OBIS code is 1.0.99.2.0.255, with Interface class as 7. The capture objects of this daily load profile are as per Table 45 and the captured attribute shall be 2 of each interface class. The capture object values will be copied into a buffer of this array automatically as per capture period which shall be statically fixed as 24 h.

c

Association access rights are as follows:

 a) *Public client* — No access to all objects.

 b) *Meter reader* — Read only for all objects.

 c) *Utility setting* — Read only for all objects.

**E-8.1 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 45. This is modeled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.5.255. The capture objects for this profile shall include the scaler — unit attributes of the parameters listed in Table 45. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**E-9 BILLING PROFILE PARAMETERS**

The billing profile parameters are listed in Table 46.

Association access rights are as follows:

 a) *Public client* — No access to all objects.

 b) *Meter reader* — Read only for all objects.

 c) *Utility setting* — Read only for all objects.

**E-9.1 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 46. This is modelled as profile generic (IC = 7) and is assigned the country specific OBIS code 1.0.94.91.6.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed in Table 46 and parameters that do not have a scaler-unit (like IC = 1) shall not be included in the capture objects list. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**E-10 GENERAL PURPOSE PARAMETERS**

The Name plate details (Table 47), and Programmable parameters (Table 48) are designated as general-purpose parameters.

**E-10.1 Name Plate Details**

The data are meter specific information.

Association access rights for name plate details are as follows:

 a) *Public client* — No access for all objects except meter serial number.

 b) *Meter reader* — Read only for all objects.

 c) *Utility setting* — Read only for all objects.

The Name plate details parameters are listed in Table 47.

This is modelled as profile generic with OBIS code = 0.0.94.91.10.255, IC = 7, Attribute = 2

**E-10.2 PROGRAMMABLE PARAMETERS**

Association access rights for programmable parameters given in Table 48 are as follows:

 a) *Public client* — No access for all objects except real time clock.

 b) *Meter reader* — Read only for all objects.

 c) *Utility setting* — Read, write for all objects.

The programmable parameters are listed in Table 48.

**E-11 EVENT REFERENCE TABLE**

**E-11.1 Events**

Any exceptional/fraud/tamper condition is considered as an Event and stored in an Event code object (OBIS = 0.0.96.11.e.255 IC = 1, values of e range from 1 to 5). The value attribute (attr-2) of this object stores identifier corresponding to the most recent event occurred in the meter. A unique identifier is assigned to occurrence and restoration of all possible events (identified so far) in the event reference tables (*see* Tables 49 to 53). Thus, the event code object will tell only about the most recent event and to get a picture of all events and associated information (at the time of event) an event log object is used. An event log object is modelled as Profile generic (OBIS = 0.0.99.98.e.255 IC = 7, values of e range from 1 to 5). The buffer attribute (attr-2) of this profile object will store (asynchronously) a new entry for every event (occurrence and restoration are considered as separate events). The capture objects for the event log object are defined in Table 54. The total no. of events to be stored shall be 20 for the power ON/OFF event and not more than 50 for all other events.

The document containing test procedure, threshold values and persistence time for event simulation shall be provided by the test requesting organization.

**E-11.2 Capture Parameters for Event as Applicable (Event Log Profile)**

Association access rights are as follows:

 a) *Public client* — No access

 b) *Meter reader* — Read only

 c) *Utility settings* — Read only

**E-11.3** Indian Event Reference Tables (Refer Table 49 to 53)

**E-11.4 Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 54. This is modelled as profile generic (IC = 7) and is assigned the country specific OBIS code 1.0.94.91.7.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed above. Parameters listed above that do not have a scaler-unit attribute shall not be included in the capture objects of this profile. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**ANNEX F**

(*Clauses* 6.1.1*,* B-5.1 *and* B-5.2*)*

## GENERAL PURPOSE PARAMETERS

1. **NAME PLATE DETAILS**

The contents of Table 30 are common to all meters. The data are meter specific information.

**F-1.1** Association access rights for name plate details are as follows:

a) *Public Client* – No access for all objects except meter serial number.

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read only for all objects.

This is modeled as profile generic with OBIS code = 0.0.94.91.10.255, IC = 7, Attribute = 2

**Table 30 Name Plate Details Parameters**

(*Clause* F-1)

|  |  |  |  |
| --- | --- | --- | --- |
|  |  **SI No. Parameter** | **OBIS Code****A B C D E F** | **Interface Class** |
|
|  |  (1) (2) | (3) (4)(5)(6)(7)(8) | (9) |
|  | 1. Meter serial number
 | 0.0.96.1.0.255 | 1 (Data) |
|  | 1. Manufacturer name
 | 0.0.96.1.1.255 | 1 |
|  | 1. Firmware version for meter
 | 1.0.0.2.0.255 | 1 |
|  | 1. Meter type (3P-3W / 3P-4W)
 | 0.0.94.91.9.255 | 1 |
|  | 1. Category
2. Current rating
3. Internal CT ratio
 | 0.0.94.91.11.2550.0.94.91.12.2551.0.0.4.2.255  | 1 1 1 |
|  | 1. Internal VT ratio
 | 1.0.0.4.3.255 |  1 |
|  | 1. Meter year of manufacture
 | 0.0.96.1.4.255 | 1 |
| **NOTE** 1) For item Sl No (iv), Value of ‘0’ indicates 3P-3W HT CT PT meters,  Value of ‘1’ indicates 3P-4W meters (applicable for already supplied meters), Value of ‘2’ indicates 3P 4W HT PT/CT meters, Value of ‘3’ indicates 3P 4W LT CT meters,  Value of ‘4’ indicates 3P 4W whole current meters.2) For Sl No. (v),C1 indicates HT (PT/CT operated) and LT (CT operated) consumer meters,C2 indicates 3 Phase 4 Wire Whole current/Direct connected consumer meters. A indicates category A meter. B indicates category B meter. 3)For Sl No. (vi), The Current rating shall be represented as Ib-Imax A. 4)For item at Sl No. (vii), Year of manufacture is mandatory, and the format is yyyy. 5) Parameters at Sl. No. (iii), (iv) are not mandatory to print on meter’s face plate. 6) Parameters at Sl. No. (vii), (viii) are not mandatory to print on meter’s face plate where these are not applicable, (fixed as 1) for whole current meters. |

1. **Programmable Parameters.**

Association access rights for programmable parameters as given in Table 31 are as follows:

a) *Public Client* – No access to all objects except real time clock.

b) *Meter Reader* – Read only for all objects.

c) *Utility Setting* – Read, write for all objects.

**Table 31 Programmable Parameters**

(*Clause* F-2)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Parameter** | **OBIS Code****A B C D E F** | **Interface Class** |
|
| (1) | (2) | (3) (4)(5)(6)(7)(8) | (9) |
|  | Real time clock, date and time | 0.0.1.0.0.255 | 8 (Clock) |
|  | Demand integration period  | 1.0.0.8.0.255 | 1 (Data) |
|  | Profile capture period | 1.0.0.8.4.255 | 1 |
|  | Single-action schedule for billing dates | 0.0.15.0.0.255 | 22 |
|    | v) Activity calendar for time zones vi) RS 485 Device address etc | 0.0.13.0.0.2550.0.22.0.0.255 | 2023 |
|  NOTES1. The parameters are programmable by the utility engineers with required access rights.
2. Unit for demand integration period and profile capture period is in ‘seconds’.
3. Programming of any of the parameters shall increment the ‘Cumulative programming count’ value.

 4)Parameter listed at Sl No. (iv) and (v) are applicable for category C meters only. 5)Sl No. (vi) programmability is applicable only for meters with RS485 ports. 6)The RTC – Time format by default shall be hh:mm:ss. 7) Parameter at Sl No. (ii) is not applicable for Category B meters.  8) Parameter at Sl No. (iv) is applicable for Category B meters. 9) Programming of activity calendar for time zones shall support time format as HH:MM, where MM shall be in line with demand integration period. All fields with “not specified” will deactivate this automatism, but partial “not specified” in some field not allowed instead use a valid value for example 0 for hundredth of seconds. 10) On activation of new time zones settings, the on – going billing cycle data will be generated and a new billing cycle shall be commenced as per new activity calendar. |
|  |

**ANNEX G**

(*Clauses* 6.1.1 *and* B-1*)*

## EVENT REFERENCE TABLE

1. **EVENTS**

Any exceptional / fraud / tamper condition is considered as an Event and stored in an Event code object (OBIS=0.0.96.11.e.255 IC=1, values of e range from 0 to 6). The value attribute (attr-2) of this object stores identifier corresponding to the most recent event occurred in the meter. A unique identifier is assigned to occurrence and restoration of all possible events (identified so far) in the event reference tables (*see* Tables 32 to 38). Thus, the event code object will tell only about the most recent event and to get a picture of all events and associated information (at the time of event) an event log object is used. An event log object is modelled as Profile generic (OBIS= 0.0.99.98.e.255 IC=7, values of e range from 0 to 6). The buffer attribute (attr-2) of this profile object will store (asynchronously) a new entry for every event (occurrence and restoration are considered as separate events). The capture objects for the event log object are defined in Table-39. The document containing test procedure, threshold values and persistence time for event simulation shall be provided by the test requesting organization.

1. **Indian Event Reference Tables**

The contents of Table 32 to 38 are common to all categories of meter.

**G-1.2 Capture Parameters for Event as Applicable (Event Log Profile)**

Association access rights are as follows:

a) *Public Client* - No access;

b) *Meter Reading* - Read only; and

 c) *Utility Settings* - Read only.

**Table 32 Indian Event Reference Table – Voltage Related**

(*Clauses* B-6.4*,* B-6.5*,* G-1 *and* G-1.1*)*

|  |  |  |
| --- | --- | --- |
| **Sl No.** |  **Event ID** | **Descriptions** |
|  |  |  |
|  | 1 | *R*-Phase – VT link missing (Missing potential) – Occurrence  |
|  | 2 | *R*-Phase – VT link missing (Missing potential) – Restoration  |
|  | 3 | *Y*-Phase – VT link missing (Missing potential) – Occurrence |
|  | 4 | *Y*-Phase – VT link missing (Missing potential) – Restoration |
|  | 5 | *B*-Phase – VT link missing (Missing potential) – Occurrence |
|  | 6 | *B*-Phase – VT link missing (Missing potential) – Restoration |
|  | 7 | Over voltage in any phase - Occurrence |
|  | 8 | Over voltage in any phase - Restoration |
|  | 9 | Low voltage in any phase - Occurrence |
|  | 10 | Low voltage in any phase - Restoration |
|  | 11 | Voltage unbalance - Occurrence |
|  | 12 | Voltage unbalance - Restoration |

NOTES

**1** These are the event conditions generally recorded in consumer meters, utilities may select any of the above event conditions based on their practice. The need and applicability of these events for other types of meters shall be considered by utility.

**2** Occurrence is considered an event.

**3** For each of the events a certain list of parameters will be captured.

**4** The list capture parameters are given in Table 39. The utility shall select the required parameters from Table 39 as per their practice.

**5** For each of the occurrence events captured, the cumulative tamper count value shall be incremented.

**6** Capture parameters mentioned in Table 39 are captured when event occurrence and restoration is logged.

**7** The attributes of each of the IC (Interface class) is to be identified while finalizing the Specification.

**8)** For 3φ/3W the reference point is Y-Phase.

**9)** Support for selective access shall be as defined in **11.3**.

**10)** Sl. No. (iii) and (iv) are not applicable for 3φ/3W meter.

**Table 33 Indian Event Reference Table – Current Related**

(*Clauses* B-6.4*,* B-6.5*,* G-1 *and* G-1.1*)*

|  |  |  |
| --- | --- | --- |
| **Sl No.** | **Event ID** | **Descriptions** |
|  |  |  |
|  | 51 | Phase – R CT reverse – Occurrence |
|  | 52 | Phase – R CT reverse – Restoration |
|  | 53 | Phase – Y CT reverse – Occurrence |
|  | 54 | Phase – Y CT reverse – Restoration |
|  | 55 | Phase – B CT reverse – Occurrence |
|  | 56 | Phase – B CT reverse – Restoration |
|  | 57 | Phase – R CT Open - Occurrence |
|  | 58 | Phase – R CT Open - Restoration |
|  | 59 | Phase – Y CT Open - Occurrence |
|  | 60 | Phase – Y CT Open - Restoration |
|  | 61 | Phase – B CT Open - Occurrence |
|  | 62 | Phase – B CT Open - Restoration |
|  | 63 | Current unbalance - Occurrence |
|  | 64 | Current unbalance - Restoration |
|  | 65 | CT bypass – Occurrence |
|  | 66 | CT bypass – Restoration |
|  | 67 | Over current in any Phase – Occurrence |
|  | 68 | Over current in any Phase – Restoration |

NOTES

**1** These are the event conditions generally recorded in consumer meters, utilities may select any of the above event conditions based on their practice. The need and applicability of these events for other types of meters shall be considered by utility.

**2**. Occurrence is considered an event

**3** For each of the events a certain list of parameters will be captured.

**4** The list capture parameters are given in Table 39. The utility shall select the required parameters from Table 39 as per their practice.

**5** For each of the occurrence events captured, the cumulative tamper count value shall be incremented.

**6** Capture parameters mentioned in Table 39 are captured when event occurrence and restoration is logged.

**7** The attributes of each of the IC (Interface class) is to be identified while finalizing the Companion Specification.

**8** For 3φ/3W the reference point is Y-Phase.

**9** Sl. No. (iii), (iv), (ix) and (x) are not applicable for 3φ/3W meter.

**10** Support for selective access shall be as defined in **11.3**.

**Table 34 Indian Event Reference Table – Power Related**

(*Clauses* B-6.4*,* B-6.5*,* G-1 *and* G-1.1*)*

|  |  |  |
| --- | --- | --- |
| **Sl No.** | **Event ID**  |  **Descriptions** |
|  | 1.
 |  |
|  |  101 | Power failure (3 phase) – Occurrence |
|  |  102 | Power failure (3 phase) – Restoration |

NOTES

**1** These are the event conditions generally recorded in consumer meters, utilities may select any of the above event conditions based on their practice. The need and applicability of these events for other types of meters shall be considered by utility.

**2** Occurrence is considered an event.

**3** For events in Table 34, date and time of event and event ID shall be captured.

**4** The attributes of each of the IC (Interface class) is to be identified while finalizing the Companion Specification.

**5)** Support for selective access shall be as defined in **11.3**.

**Table 35 Indian Event Reference Table – Transaction Related**

(*Clauses* B-6.4*,* B-6.5*,* G-1 *and* G-1.1*)*

|  |  |  |
| --- | --- | --- |
| **Sl No.** | **Event ID**  | **Descriptions** |
|  |  |  |
|  | 151 | Real time clock – date and time |
|  | 152 | Demand integration period  |
|  | 153 | Profile capture period |

|  |  |  |
| --- | --- | --- |
|  | 154 | Single-action schedule for billing dates |
|  vi) | 155156 | Activity calendar for time zonesRS485 device address, etc |

NOTES

**1** These are the event conditions generally recorded in consumer meters, utilities may select any of the above event conditions based.

on their practice. The need and applicability of these events for other types of meters shall be considered by utility.

**2** Occurrence is considered as an event.

**3** Date and time of event and event ID shall be captured.

**4** RS 485 device address programmability shall be present in MR and also in US mode.

**5** Device address programmability is only applicable for meters with RS485 ports.**6)** Support for selective access shall be as defined in **11.3**.

**Table 36 Indian Event Reference Table – Others**

(*Clauses* B-6.4, B-6.5, G-1 *and* G-1.1)

|  |  |  |
| --- | --- | --- |
| **Sl No** | **Event ID**  | **Descriptions** |
|  |  |  |
|  |  201 | Influence of permanent magnet or ac/dc electromagnet - Occurrence |
|  |  202 | Influence of permanent magnet or ac/dc electromagnet - Restoration |
|  |  203 | Neutral disturbance event logging due to HF or dc or alternate method as implemented in the meter — Occurrence’ |
|  |  204 | Neutral disturbance event logging due to HF or dc or alternate method as implemented in the meter — Restoration’ |
|  |  205 | Very low PF - Occurrence |
|  |  206 | Very low PF - Restoration |

NOTES

**1** These are the event conditions generally recorded in consumer meters, utilities may select any of the above event conditions based on their practice. The need and applicability of these events for other types of meters shall be considered by utility.

**2** Occurrence is considered an event.

**3** For each of the events a certain list of parameters will be captured.

**4** The list capture parameters are given in Table 39. The utility shall select the required parameters from Table 39 as per their practice.

**5** For each of the occurrence events captured, the cumulative tamper count value shall be incremented.

**6** Capture parameters mentioned in Table 39 are captured when event occurrence and restoration is logged.

**7** The attributes of each of the IC (Interface class) are to be identified while finalizing the Companion Specification.

**8)** For 3φ/3W the reference point is Y-Phase.

**9)** Support for selective access shall be as defined in **11.3**.

**Table 37 Indian Event Reference Table – Non-rollover Events**

(*Clauses* B-6.4*,* B-6.5*,* G-1 *and* G-1.1*)*

|  |  |  |
| --- | --- | --- |
| **Sl.No.** | **Event ID** | **Descriptions** |
|  |  |  |
|  | 251 | Meter cover opening – Occurrence |

NOTES

**1** This event condition is generally recorded in consumer meters; utilities may select the above event condition based on their

practice. The need and applicability of the event for other types of meters shall be considered by utility.

**2** Occurrence is considered an event.

**3** Date and time of event and event ID shall be captured on event occurrence.

**Table 38 Indian Event Reference Table – Control Events**

(*Clauses* B-6.4*,* B-6.5*,* G-1 *and* G-1.1*)*

|  |  |  |
| --- | --- | --- |
| **Sl No.** | **Event ID** | **Descriptions** |
| (1) |  (2) | (3) |
|  | 301 | Meter load disconnected |
|  | 302 | Meter load connected |

NOTES

**1** These are the event conditions generally recorded in consumer meters, utilities may select any of the above event conditions based on their practice. The need and applicability of these events for other types of meters shall be considered by utility.

**2** Occurrence is considered an event.

**3** Date and time of event and event ID shall be captured.

**Table 39 Capture Parameters for Events**

(*Clauses* B-6.4*,* B-6.5 *and* G-1*)*

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **Sl No** | **Parameter**  |  |  **OBIS Code** |  | **Interface class** |
|  |  |  **A** |  **B** |  **C** |  **D** |  **E** |  **F** |  |
|  |  |  |  |  |  |  |  |  |
|  | Date and time of event | 0 | 0 | 1 | 0 | 0 | 255 | 8 (Clock) |
|  | Event Code | 0 | 0 | 96 | 11 | e | 255 | 1 (Data) |
|  | Current, *I*R  | 1 | 0 | 31 | 7 | 0 | 255 | 3 (Register) |
|  | Current, *I*Y  | 1 | 0 | 51 | 7 | 0 | 255 | 3 (Register) |
|  | Current, *I*B  | 1 | 0 | 71 | 7 | 0 | 255 | 3 (Register) |
|  | Voltage, *V*RN (3Ф/4W) | 1 | 0 | 32 | 7 | 0 | 255 | 3 (Register) |
|  | Voltage – *V*YN (3Ф/4W) | 1 | 0 | 52 | 7 | 0 | 255 | 3 (Register) |
|  | Voltage – *V*BN (3Ф/4W) | 1 | 0 | 72 | 7 | 0 | 255 | 3 (Register) |
|  | Voltage - *V*RY (3Ф/3W) | 1 | 0 | 32 | 7 | 0 | 255 | 3 (Register) |
|  | Voltage – *V*YB (3Ф/3W) | 1 | 0 | 52 | 7 | 0 | 255 | 3 (Register) |
|  | Power factor, R -phase  | 1 | 0 | 33 | 7 | 0 | 255 | 3 (Register) |
|  | Power factor, Y- phase  | 1 | 0 | 53 | 7 | 0 | 255 | 3 (Register) |
|  | Power factor, B -phase  | 1 | 0 | 73 | 7 | 0 | 255 | 3 (Register) |
|  | Cumulative energy, kWh  | 1 | 0 | 1 | 8 | 0 | 255 | 3 (Register) |

NOTES

**1** For each of the events a certain list of parameters will be captured.

**2** The list of capture parameters is given. The utility shall select the required parameters from the table as per their practice.

**3** Capture parameters mentioned in the table are to be captured when event occurrence and restoration is logged.

**4** For 3φ/3W the reference point is *Y*-Phase.

**5)** The RTC — Time format by default shall be hh:mm.

6) e range from 0 to 6.

1. **Scaler Profile**

This profile is meant for capturing the scaler-unit of each of the parameter listed in Table 39. This is modelled as profile generic (IC=7) and is assigned the country specific OBIS code 1.0.94.91.7.255. The capture objects for this profile shall include the scaler-unit attributes of the parameters listed above. Parameters listed above that do not have a scaler-unit attribute shall not be included in the capture objects of this profile. The profile buffer shall have only one entry. This profile is not required to be updated periodically.

**ANNEX H**

(*Clause* 2)

**LIST OF REFERRED INDIAN/INTERNATIONAL STANDARDS**

|  |  |
| --- | --- |
| *Indian/ International Standard*ISS 14697 : 1999 | *Title* ac static transformer operated watthour and var-hour meters, class 0.2 S, 0.5 S and 1.0 S **—** Specification |
| DLMS UA 1000-1 ed.9,2009 | Blue book, COSEM identification system and interface classes |
| DLMS UA 1000-2 ed.7,2007 | Green book, DLMS/COSEM architecture and protocols |
| DLMS UA 1002: ed.1,2003 | White book, COSEM Glossary of terms |
| DLMS UA 1001-1:2007 ed-3IS/IEC 62056-21:2002IS/IEC 62056-42:2002IS/IEC 62056-46:2007IS/IEC 62056-47:2006IS/IEC 62056-53:2006 | Yellow Book, companion testing processElectricity metering: Data exchange for meter reading, tariff and load control: Part 21 Direct local data exchangeElectricity metering: Data exchange for meter reading, tariff and load control: Part 42 Physical layer services and procedures for connection-oriented asynchronous data exchangeElectricity metering: Data exchange for meter reading, tariff and load control: Part 46 Data link layer using HDLC protocolElectricity metering Data exchange for meter reading tariff and load control: Part 47 COSEM transport layer for IPv4 networkElectricity metering: Data exchange for meter reading, tariff and load control: Part 53 COSEM application layer |
| IS/IEC 62056-5-1: 2006  | Electricity metering: Part 61 Data exchange for meter reading, tariff and load control Object identification system (OBIS) |
| IS/IEC 62056-6-2:2006 | Electricity metering: Data exchange for meter reading, tariff and load controlPart 62: Interface classes |
| IEC/TR 62051:1999IS/IEC/TR62051-1:2004 | Electricity metering **—** Glossary oftermsElectricity metering: Data exchange for meter reading, tariff and load control **—** Glossary of terms: Part 1 Terms related to data exchange with metering equipment using DLMS/COSEM |
|  |  |
| NIST Special Publication 800-38D, Nov 2007 | Recommendation for block cipher modes of operation: Galois/Counter Mode (GCM) and GMAC  |
| NIST Federal ProcessingStandardsPublication 197:Nov 2001 | Advanced encryption standardInformation (AES) |
| NIST Federal Information Processing Standards Publication 199:2004 | Standards for security categorizationof federal information andProcessing information systems |
|  |  |
|  |  |
| IETF Request For Circulation (RFC) - 3394:Sept, 2002  | Advanced encryption standard (AES) key wrap algorithm (Informative) |
|  |  |

**ANNEX J**

(*Clause* 3.6)

**HHU (MRI) CONSIDERATION**

**J-1 HHU (MRI) CONSIDERATION**

Communication standards in the Indian metering scenario require supporting considerations for the utilization of those standards in HHUs (Hand held units synonymous with MRI or CMRI). This Annex provides a suitable approach to the implementation of the IEC-62056 standards and this Indian Companion Specification in such devices.

**J-1.1** The terms of this suggested implementation are as below:

a) HHUs may retrieve data from DLMS/COSEM Meters conforming to this standard using the communication ports.

b) HHUs shall exclusively use the Meter Reading association (MR) and shall support all the features and specifications listed in this specification for the MR Association.

1. HHUs shall have the same data access rights that are available to the MR association, as that available for remote meter reading.
2. HHU when acting as a server shall support the client addresses and security methods of the Meter Reading (MR) Association.
3. HHUs shall provide a DLMS/COSEM server interface to the BCS (Base Computer System – the Data collection software) over a suitable communication medium (local serial port implementing the DLMS/COSEM CO 3-layer stack is suggested).
4. HHUs shall internally map the individual meter data to Logical Devices (one Logical Device for each meter). Inside each Logical Device the structure and naming of the data shall be the same as that retrieved from the meter
5. For each logical device the DLMS/COSEM server shall support one association with properties, objects, and access rights adequate for transferring the stored data of the corresponding meter to the BCS in an efficient manner. The server within the HHU is not required to support ad-hoc access or selective access to the data that differs from the requests which were earlier used to read the data from the meter.
6. The BCS shall maintain a mapping table that maps the individual meter identifications (the same IDs that are used to identify the meter during remote meter reading) to Logical Device addresses. During upload of data from HHU to BCS, the BCS shall query each Logical device to download the data of each meter over the local serial port
7. The mapping table described in Item I-1.6 above shall require that the Logical device addresses allocated to each meter are at least unique across all meters that are to be retrieved using one HHU. Other HHUs may re-use the same addressing from their own range of allocated meters. The BCS shall take care to ensure that the re-use of addresses does not create conflicts in Meter identification.

**ANNEX K**

**(***Clause* 3.23**)**

**CONFORMANCE TESTING**

**K-1** Meters claiming conformance to this specification will be required to

1. “Conform to the DLMS/COSEM base standards (IEC 62056) as certified by the conformance test tool (CTT)/” Make in India - Indigenous test tool: **SMITHA-BSMPA** (Smart Meter Integrated Testing and Higher Analysis - Bharat Smart Meter Protocol Analysis)”
2. conform to the specific requirements and constraints of this standard as certified by CPRI or any other laboratory having facilities for the purpose.

Note: CTT to be used in parallel with SMITHA-BSMPA for another two years till 31/Dec/2025.

**K-2** This certification shall ensure.

a) all mandatory parameters applicable to the category of the meter under test are implemented.

b) all data types where specified are conforming to this document.

c) all application associations are implemented as specified in this standard with all specified services supported;

d) association object lists conform to this document with access rights and OBIS codes as specified here; and

e) event related DLMS objects are implemented with Event identifiers as specified in the Event reference tables in this standard.

**K-2.1** The test report from an accredited laboratory and having membership with DLMS UA shall be considered as proof of conformance of protocol implementation.

**K-2.2** Systems once created in accordance with this specification and contemporary standards, shall be deemed acceptable, provided such systems are tested and certified through standard evaluation process.

**‘**List of tests for various categories of meters are given in Tables 40, 41 and 42’.

**Table 40 List of Tests for Category A Meter**

**(Clause K-2)**

| **Item No.****(1)** | **Compliance Test** (2) | **Ref to Clause**(3) |
| --- | --- | --- |
| 1.0 | Conformance to DLMS/COSEM (IEC 62056) | K – 1 (a) |
| 2.0 | Parameter verification: |  |
| 2.1 | SNRM/UA | 4.1 and 4.2 |
| 2.2 | Object list download  | 5.1 and 5.2 |
| 2.3 | Association properties  | 5.1 and 5.2 |
| 2.4 | Simultaneous operation | 4.3 |
| 2.5 | Security: | 7.5 |
| 2.5.1 | Lowest level security secret | 7.5.1.1 |
| 2.5.2 | Low level security (LLS) secret  | 7.5.1.2 |
| 2.5.3 | High level security (HLS) secret  | 7.5.1.3 |
| 2.6 | Parameter list: |
| 2.6.1 (a) | Instantaneous parameters | C-4 and Table 22 |
| 2.6.1 (b) | Snapshot of instantaneous parameters | C-4.1 |
| 2.6.1 (c) | Scaler profile | C-4.2 |
| 2.6.2 | Block load profile parameters | C-5 and Table 23 |
| 2.6.3 | Selective access by range for block load profile  | 11.3 |
| 2.7 | General purpose parameters: |
| 2.7.1 | Name plate details | F-1 and Table 30 |
| 2.7.2 | Programmable parameters | F-2 and Table 31  |
| 2.8 | Event code and event logging: | 8.1, 8.2, G-1, G-2 and Table 39 |
| 2.8.1 | Indian event reference table - Voltage related | Table 32  |
| 2.8.2 | Indian event reference table - Current related | Table 33  |
| 2.8.3 | Indian event reference table - Power related | Table 34 |
| 2.8.4 | Indian event reference table - Transaction related | Table 35 |
| 2.8.5 | Indian event reference table - Other | Table 36  |
| 2.8.6 | Indian event reference table - Non-Roll Over | Table 37 |
| 2.8.7 | Indian event reference table - Control | Table 38 |
| 2.9 | Selective access by entry for event log profile  | 11.3 |
| 2.10 | Billing period  | C-7, Table 23A |
| 2.11 | Billing period counter | C-7, Table 23A |

**Table 41 List of Tests for Category B Meter**

(*Clause* K-2)

| **Item No.****(1)** | **Compliance Test** (2) | **Ref to Clause**(3) |
| --- | --- | --- |
| 1.0 | Conformance to DLMS/COSEM (IEC 62056) | K – 1 (a) |
| 2.0 | Parameter verification: |  |
| 2.1 | SNRM/UA | 4.1 and 4.2 |
| 2.2 | Object list download  | 5.1 and 5.2 |
| 2.3 | Association properties  | 5.1 and 5.2 |
| 2.4 | Simultaneous operation | 4.3 |
| 2.5 | Security | 7.5 |
| 2.5.1 | Lowest level security secret | 7.5.1.1 |
| 2.5.2 | Low level security (LLS) secret  | 7.5.1.2 |
| 2.5.3 | High level security (HLS) secret  | 7.5.1.3 |
| 2.6 | Parameter list: |
| 2.6.1 (a) | Instantaneous parameters | D-3.1 and Table 24 |
| 2.6.1 (b) | Snapshot of instantaneous parameters | D-3.3 |
| 2.6.1 (c) | Scaler profile | D-3.4 |
| 2.6.2 | Block load profile parameters | D-4 and Table 25 |
| 2.7 | Selective access by range for block load profile  | 11.3 |
| 2.8 | Daily load profile parameters | D-5 and Table 26 |
| 2.9 | Selective access by range for daily load profile | 11.3 |
| 2.10 | General purpose parameters: |
| 2.10.1 | Name plate details | F-1 and Table 30 |
| 2.10.2 | Programmable parameters | F-2 and Table 31 |
| 2.11 | Event code and event logging: | 8.1, 8.2, G-1, G-2 and Table 39 |
| 2.11.1 | Indian event reference table - Voltage related | Table 32  |
| 2.11.2 | Indian event reference table - Current related | Table 33  |
| 2.11.3 | Indian event reference table - Power related | Table 34 |
| 2.11.4 | Indian event reference table - Transaction related | Table 35 |
| 2.11.5 | Indian event reference table - Other | Table 36  |
| 2.11.6 | Indian event reference table - Non-Roll Over | Table 37 |
| 2.11.7 | Indian event reference table - Control | Table 38 |
| 2.12 | Selective access by entry for event log profile | 11.3 |
| 2.13 | Billing period  | D-6, Table 56 |
| 2.14 | Billing period counter | D-6, Table 56 |

**Table 42 List of tests for Category C Meter**

(*Clause* K-2)

| **Item No.****(1)** | **Compliance Test** (2) | **Ref to Clause**(3) |
| --- | --- | --- |
| 1.0 | Conformance to DLMS/COSEM (IEC 62056) | K – 1 (a) |
| 2.0 | Parameter verification: |  |
| 2.1 | SNRM/UA | 4.1 and 4.2 |
| 2.2 | Object list download  | 5.1 and 5.2 |
| 2.3 | Association properties  | 5.1 and 5.2 |
| 2.4 | Simultaneous operation | 4.3 |
| 2.5 | Security: | 7.5 |
| 2.5.1 | Lowest level security secret | 7.5.1.1 |
| 2.5.2 | Low level security (LLS) secret  | 7.5.1.2 |
| 2.5.3 | High level security (HLS) secret  | 7.5.1.3 |
| 2.6 | ToU setting  | 9  |
| 2.7 | Billing period  | 10.1 and 10.2  |
| 2.8 | Billing period counter | 11.2.1 and 11.2.2  |
| 2.9 | Parameter list: |
| 2.9.1 (a) | Instantaneous parameters | E-3, E-3.1 and Table 27 |
| 2.9.1 (b) | Snapshot of instantaneous parameters | E-3.2 |
| 2.9.1 (c) | Scaler profile | E-3.3 |
| 2.9.2 | Block load profile parameters | E-4 and Table 28  |
| 2.9.3 | Selective access by range for block load profile  | 11.3 |
| 2.10 | Billing profile parameters | E-5 and Table 29  |
| 2.11 | Selective access by entry for billing profile  | 11.3 |
| 2.12 | General purpose parameters: |
| 2.12.1 | Name plate details | F-1 and Table 30 |
| 2.12.2 | Programmable parameters | F-2 and Table 31 |
| 2.13 | Event code and event logging: | 8.1, 8.2, G-1, G-2 and Table 39 |
| 2.13.1 | Indian event reference table - Voltage related | Table 32 |
| 2.13.2 | Indian event reference table - Current related | Table 33  |
| 2.13.3 | Indian event reference table - Power related | Table 34 |
| 2.13.4 | Indian event reference table - Transaction related | Table 35 |
| 2.13.5 | Indian event reference table - Other | Table 36 |
| 2.13.6 | Indian event reference table - Non-Roll Over | Table 37 |
| 2.13.7 | Indian event reference table - Control | Table 38 |
| 2.14 | Selective access by entry for event log profile  | 11.3 |
| 2.15 | Daily load profile parameters | E-12 |

**Table 43 Instantaneous Parameters**

(*Clause* E-6.1, E-6.2 *and* E-6.3)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** (1)  | **Parameter** (2)  | **OBIS code A.B.C.D.E.F** (3)  | **Interface Class/Attributes** (4)  |

|  |  |  |  |
| --- | --- | --- | --- |
| i)  | Real time clock – date and time  | 0.0.1.0.0.255  |  8/2  |
| ii)  | Voltage  | 1.0.12.7.0.255  |  3/2  |
| iii)  | Phase current  | 1.0.11.7.0.255  |  3/2  |
| iv)  | Neutral current  | 1.0.91.7.0.255  |  3/2  |
| v)  | Signed power factor  | 1.0.13.7.0.255  |  3/2  |
| vi)  | Frequency – Hz  | 1.0.14.7.0.255  |  3/2  |
| vii)  | Apparent Power – KVA  | 1.0.9.7.0.255  |  3/2  |
| viii)  | Active Power – kW  | 1.0.1.7.0.255  |  3/2  |
| ix)  | Cumulative Energy, kWh  | 1.0.1.8.0.255  |  3/2  |
| x)  | Cumulative Energy, kVAh  | 1.0.9.8.0.255  |  3/2  |
| xi)  | Maximum Demand, kW  | 1.0.1.6.0.255  |  4/2, 5  |
| xii)  | Maximum Demand, kVA  | 1.0.9.6.0.255  |  4/2, 5  |
| xiii)  | Cumulative power ON duration in minutes  | 0.0.94.91.14.255  |  3/2  |
| xiv)  | Cumulative tamper count  | 0.0.94.91.0.255  |  1/2  |
| xv)  | Cumulative billing count  | 0.0.0.1.0.255  |  1/2  |
| xvi)  | Cumulative programming count  | 0.0.96.2.0.255  |  1/2  |

NOTES

**1** The above list is identified for the purpose of communication to HOST or HHU.

**2** The utilities may choose, based on needs, additional parameters for display purpose only.

**3** The parameters at Sl. No. xiii to xvi hold cumulative values at that instant from the date of manufacturing or installation of meter as the case may be.

**4** Item at Sl. No. xv, refers to the Billing Period Counter.

**5** The RTC-Time format by default shall be HH:MM:SS

**6** Signed power factor shall be verified at rated voltage, rated current and rated frequency at 0.5 lag and 0.8 lead.

**7** Power and Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.

8 Minimum parameters that the meter should have are i, ii, iii, iv, v, vi, viii, ix, xi, xiii, xiv, xv and xvi. The other parameters mentioned in the table are optional for buyers/utilities to choose.

9) In case the meter is powered up with Voltage only, Sl.No. (v) should store the value as UPF.

**Table 44 Block Load profile parameters**

(*Clause* E-7 *and* E-7.1)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** (1)  | **Parameter**(2)  | **OBIS code A.B.C.D.E.F** (3)  | **Interface Class/Attributes** (4)  |

|  |  |  |  |
| --- | --- | --- | --- |
| i)  | Real time clock – date and time  | 0.0.1.0.0.255  |  8/2  |
| ii)  | Average voltage  | 1.0.12.27.0.255  |  3/2  |
| iii)  | Block energy, kWh  | 1.0.1.29.0.255  |  3/2  |
| iv)  | Block energy, kVAh  | 1.0.9.29.0.255  |  3/2  |

NOTES:

**1** The parameters listed in this table are for load survey purpose and are logged as per the block period time.

**2** For parameters at Sl. No. ii, the value shall be averaged over the integration period and stored at the end of that time block.

**3** The parameters at Sl. No.iii and iv are the actual energy consumption during that time block.

**4** Support for selective access shall be as defined in **11.3**.

**5** The RTC-time format by default shall be HH:MM.

**6** Energy related parameters shall be verified at UPF, 0.5 lag and 0.8 lead.

**7** The time stamp shall be at the end of the capture period (Ist entry value is 00:15 or 00:30 minutes as applicable and last entry value is 00:00 Hrs. next day).

 8 Minimum parameters that the meter should have are i and iii. The other parameters mentioned in the table are optional for buyers/utilities to choose.

**Table 45 Daily Load profile parameters**

(*Clause* E-8*and* E-8.1)

|  |  |  |  |
| --- | --- | --- | --- |
| Sl No. | **Parameter** | **OBIS Code** | **Interface Class/Attribute** |
|  |  | A | B | C | D | E | F |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |
| i) | Real time clock, date and time | 0 | 0 | 1 | 0 | 0 | 255 | 8/2 |
| ii) | Cumulative energy, kWh | 1 | 0 | 1 | 8 | 0 | 255 | 3/2 |
| iii) | Cumulative energy, kVAh | 1 | 0 | 9 | 8 | 0 | 255 | 3/2 |
| NOTES: **1** The parameters listed in this table are meant for billing purpose and shall be logged at midnight (00 h). **2** The storage time for these parameters is the same as Block load survey. **3** Support for selective access shall be as defined in **11.3**4 Minimum parameters that the meter should have are i and ii. The other parameters mentioned in the table are optional for buyers/utilities to choose. |  |

**Table 46 Billing profile parameters**

(*Clause* E-9*and* E-9.1)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** (1)  | **Parameter** (2)  | **OBIS code A.B.C.D.E.F** (3)  | **Interface Class/Attribute** (4)  |
| i)  | Billing date  | 0.0.0.1.2.255  | 3/2 |
| ii)  | Average power factor for billing period  | 1.0.13.0.0.255  | 3/2 |
| iii)  | Cumulative energy, kWh  | 1.0.1.8.0.255  | 3/2 |
| iv)  | Cumulative energy, kWh for TZ1  | 1.0.1.8.1.255  | 3/2 |
| v)  | Cumulative energy, kWh for TZ2  | 1.0.1.8.2.255  | 3/2 |
| vi)  | Cumulative energy, kWh for TZ3  | 1.0.1.8.3.255  | 3/2 |
| vii)  | Cumulative energy, kWh for TZ4  | 1.0.1.8.4.255  | 3/2 |
| viii)  | Cumulative energy, kVAh  | 1.0.9.8.0.255  | 3/2 |
| ix)  | Cumulative energy, kVAH for TZ1  | 1.0.9.8.1.255  | 3/2 |
| x)  | Cumulative energy, kVAH for TZ2  | 1.0.9.8.2.255  | 3/2 |
| xi)  | Cumulative energy, kVAH for TZ3  | 1.0.9.8.3.255  | 3/2 |
| xii)  | Cumulative energy, kVAH for TZ4  | 1.0.9.8.4.255  | 3/2 |
| xiii)  | MD, kW  | 1.0.1.6.0.255  | 4/2,5 |
| xiv)  | MD, kVA  | 1.0.9.6.0.255  | 4/2,5 |
| xv) | Billing Power ON duration in Minutes | 0.0.94.91.13.255 | 3/2 |
|  |  |  |  |

NOTES

**1** The data shall be stored up to 6 billing cycles. The billing profile is modelled as Profile generic (IC = 7) object with OBIS Code 1.0.98.1.0.255. The capture objects of this billing profile shall be as per Table 46. The capture object values will be copied into buffer of this object either automatically or asynchronously. The capture period is set to zero, billing action is controlled by billing dates as provided in clause 10 and Table 48.

 **2** Support for selective access shall be as defined in **11.3**.

**3** The current cycle billing parameters shall be readable as the values of the latest billing period, on demand. This shall be in addition to the last 6 billing period data which shall be available in the profile buffer as the last 6 entries in the buffer.

**4** The captured attributes in the case of Interface Class 4 (Extended register) used for MD values will be attributes 2 and 5 (Value and Time stamp).

**5** The Billing Date - Time format by default shall be HH:MM.

**6** Minimum parameters that the meter should have are i, iii, xiii and xv. The other parameters mentioned in the table are optional for buyers/utilities to choose.

**Table 47 Name plate details**

(*Clause* E-10*and* E-10.1)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.**(1)  | **Parameter**(2)  | **OBIS Code A.B.C.D.E.F** (3)  | **Interface Class**(4)  |
| i)  | Meter serial number  | 0.0.96.1.0.255  |  1 (Data)  |
| ii)  | Manufacturer name  | 0.0.96.1.1.255  |  1  |
| iii)  | Firmware version for meter  | 1.0.0.2.0.255  |  1  |
| iv)  | Meter type  | 0.0.94.91.9.255  |   1  |
| v)  | Category  | 0.0.94.91.11.255  |   1  |
| vi)  | Current rating  | 0.0.94.91.12.255  |   1  |
| vii)  | Meter year of manufacture  | 0.0.96.1.4.255  |   1  |

NOTES

**1** For item Sl. No (iv) a value of 5 indicates 1P-2W.

**2** For item (v) a value C3 indicates Single phase whole current meter.

**3** For item (vi) shall indicate current range Ib-Imax A.

**4** For item at Sl. No. (vii) year is mandatory and the format is yyyy.

**Table 48 Programmable Parameters**

(*Clause* E-10*and* E-10.2)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.**(1) | **Parameter**(2) | **OBIS Code A.B.C.D.E.F**(3) | **Interface Class** (4) |
| i)  | Real Time Clock – Date and Time  | 0.0.1.0.0.255  | 8 |
| ii)  | Demand Integration Period  | 1.0.0.8.0.255  | 1 |
| iii)  | Profile Capture Period  | 1.0.0.8.4.255  | 1 |
| iv)  | Single-action Schedule for Billing Dates  | 0.0.15.0.0.255  | 22 |
| v)  | Activity Calendar for Time Zones  | 0.0.13.0.0.255  | 20 |

NOTES

**1** The parameters are programmable by the utility engineers with required access rights.

**2** Unit for Demand Integration Period and Profile capture period is in “seconds”. The Demand Integration Period shall be 1800 seconds (default) and programmable to 900 seconds. The Profile capture period shall be 1800 seconds (default) and programmable to 900 or 3600 seconds.

**3** On change of time zones settings, the on-going billing cycle data will be generated, and a new billing cycle shall be commenced as per new activity calendar.

**4** All days in a year are considered as uniform day profile for single phase meter.

**5** Programming of any of the parameters shall increment the “Cumulative programming count” value.

**6** The RTC - Time format by default shall be HH:MM:SS.

**7**.

Programming of activity calendar for time zones shall support time format as HH:MM, where MM shall be in line with demand integration period. All fields with “not specified” will deactivate this automatism, but partial “not specified” in some field not allowed instead use a valid value for example 0 for hundredth of seconds.

**Table 49 Indian Event Reference Table — Current Related**

**(***Clause* E-11.1 *to* E-11.4**)**

|  |  |  |
| --- | --- | --- |
| **Sl No.**  | **Event ID**  | **Descriptions**  |
| (1)  | (2)  | (3)  |
| i)  | 69  | Earth Loading — Occurrence  |
| ii)  | 70  | Earth Loading —Restoration  |

NOTES

**1** Occurrence / Restoration are considered as separate events.

**2** For each of the events a certain list of parameters shall be captured as per **Table 54**.

**3** For each of the occurrence event captured, the cumulative tamper count value shall be incremented.

**4** Support for selective access shall be as defined in **11.3**.

**Table 50 Indian Event Reference Table — Power Related**

**(***Clause* E-11.1 *to* E-11.4**)**

|  |  |  |
| --- | --- | --- |
| **Sl No.**  | **Event ID**  | **Descriptions**  |
| (1)  | (2)  | (3)  |
| i)  | 101  | Power failure — Occurrence  |
| ii)  | 102  | Power failure — Restoration  |

NOTES

**1** Occurrence / Restoration are considered as separate events.

**2** For these events only date and time and event code shall be captured**.**

**3** Support for selective access shall be as defined in **11.3**.

**Table 51 Indian Event Reference Table — Transaction Related**

*(Clause* E-11.1 *to* E-11.4)

|  |  |  |
| --- | --- | --- |
| **Sl No.**  | **Event ID**  | **Descriptions**  |
| (1)  | (2)  | (3)  |
| i)  | 151  | Real time clock – date and time  |
| ii)  | 152  | Demand integration period  |
| iii)  | 153  | Profile capture period  |
| iv)  | 154  | Single-action schedule for billing dates  |
| v)  | 155  | Activity calendar for time zones  |

NOTES

**1** Occurrence is considered as separate events.

**2** For these events only date and time and event code shall be captured**.**

**3** Support for selective access shall be as defined in **11.3**.

**Table 52 Indian Event Reference Table — Others**

(*Clause* E-11.1 *to* E-11.4)

|  |  |  |
| --- | --- | --- |
| **Sl No.**  | **Event ID**  | **Descriptions**  |
| (1)  | (2)  | (3)  |
| i)  | 201  | Influence of permanent magnet or AC/ DC electromagnet – Occurrence  |
| ii)  | 202  | Influence of permanent magnet or AC/ DC electromagnet – Restoration  |
| iii)  | 203  | DC signal injection in source/load neutral terminal of the meter through diode / rectifier or neutral disturbance – HF - occurrence  |
| iv)  | 204  | DC signal injection in source/load neutral terminal of the meter through diode / rectifier or neutral disturbance – HF - Restoration  |
| v)  | 207  | Single wire operation (neutral missing) – Occurrence  |
| vi)  | 208  | Single wire operation (neutral missing) – Restoration  |

NOTES

**1** Occurrence / Restoration are considered as separate events.

**2** For each of the events a certain list of parameters shall be captured as per Table 54.

**3** For each of the occurrence events captured, the cumulative tamper count value shall be incremented.

**4** Support for selective access shall be as defined in **11.3**.

**Table 53 Indian Event Reference Table — Non-Roll Over Events**

**(*Clause* E-11.1 *to* E-11.4)**

|  |  |  |
| --- | --- | --- |
| **Sl No.**  | **Event ID**  | **Descriptions**  |
| (1)  | (2)  | (3)  |
| i)  | 251  | Meter Cover Opening – Occurrence  |

NOTES

**1** Occurrence is considered as separate events.

**2** For these events only date and time and event code shall be captured**.**

**Table 54 Capture Parameters for Events**

(*Clause* E 11.1 *to* E 11.4)

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Sl No.**  | **Parameter**  | **A**  | **B**  | **C**  | **D**  | **E**  | **F**  | **IC**  |
| (1)  | (2)  | (3)  | (4)  | (5)  | (6)  | (7)  | (8)  | (9)  |
| i)  | Date and Time of event  | 0  | 0  | 1  | 0  | 0  | 255  | 8  |
| ii)  | Event Code  | 0  | 0  | 96  | 11  |  e  | 255  | 1  |
| iii)  | Current  | 1  | 0  | 94  | 91  | 14  | 255  | 3  |
| iv)  | Voltage  | 1  | 0  | 12  | 7  | 0  | 255  | 3  |
| v)  | Power Factor  | 1  | 0  | 13  | 7  | 0  | 255  | 3  |
| vi)  | Cumulative Energy – kWh  | 1  | 0  | 1  | 8  | 0  | 255  | 3  |

NOTES

**1** Capture parameters mentioned in the table are to be captured when event occurrence and restoration is logged.

**2** Sl. No. iii) is instantaneous current used for energy consumption.

**3** For event capture, RTC-Time format shall be HH:MM.

**4.** for SI No.(ii), col 7, e range from1 to 5.

**Table 55 List of Tests for Category C3 Meter (Single Phase Whole current Meter)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sl No. |

|  |
| --- |
| **Item No.** |

 | **Particulars of Test** | **Clause Reference No.** |
|  |  | **Compliance Test** |  |
| i)  | 1.0  | Conformance to DLMS/COSEM (IEC 62056)  | **K – 1 a)**  |
| ii)  |  | Parameter Verification: |  |
| iii)  | 2.0  | SNRM/UA  | **4.1 and 4.2**  |
| iv)  | 3.0  | Object list download  | **5.1 and 5.2**  |
| v)  | 4.0  | Association properties  | **5.1 and 5.2**  |
| vi)  | 5.0  | Simultaneous operation  | **4.3**  |
| vii)  | 6.0  | Security:  | **7.5**  |
| viii)  | (a)  | Lowest Level Security Secret  | **7.5.1.1**  |
| ix)  | (b)  | Low Level Security (LLS) Secret  | **7.5.1.2**  |
| x)  | (c)  | High Level Security (HLS) Secret  | **7.5.1.3**  |
| xi)  | 7.0  | Parameter list:  |  |
| xii)  | (a)  | Instantaneous Parameters  | **E-6.1 and Table 43**  |
| xiii)  | (b)  | Snap Shot of Instantaneous Parameters  | E-6.2  |
| xiv)  | (c)  | Scaler Profile  | E-6.3  |
| xv)  | 8.0  | Block Load Profile Parameters  | **E-7, E-7.1 and Table 44**  |
| xvi)  | 9.0  | Selective access by Range for Block Load Profile  | **11.3**  |
| xvii)  | 10.0  | Daily Load Profile Parameters  | **E-8, E-8.1 and Table 45**  |
| xviii)  | 11.0  | Selective access by Range for Daily Load Profile  | **11.3**  |
| xix)  | 12.0  | ToU setting  | **9**  |
| xx)  | 13.0  | Billing Profile Parameters  | **E-9, E-9.1 and Table 46**  |
| xxi)  | 14.0  | Billing Period  | **10.1 and 10.2**  |
| xxii)  | 15.0  | Billing Period Counter  | **11.2.1 and 11.2.2**  |
| xxiii)  | 16.0  | Selective access by Entry for Billing Profile  | **11.3** |
| xxiv)  | 17.0  | General Purpose Parameters:  | **E-10**  |
| xxv)  | (a)  | Name Plate Details  | **E-10.1 and Table 47**  |
| xxvi)  | (b)  | Programmable Parameters  | **E-10.2 and Table 48**  |
| xxvii)  | 18.0  | Event code and Event logging:  | **8.1, 8.2, E-11, E-11.1 to E11.4 and Table 54**  |
| xxviii)  | (a)  | Indian Event Reference Table - Current Related  | **Table 49**  |
| xxix)  | (b)  | Indian Event Reference Table - Power Related  | **Table 50**  |
| xxx)  | (c)  | Indian Event Reference Table - Transaction Related  | **Table 51**  |
| xxxi)  | (d)  | Indian Event Reference Table – Others  | **Table 52**  |
| xxxii)  | (e)  | Indian Event Reference Table - Non-Roll Over  | **Table 53**  |
| xxxiii)  | 19.0  | Selective access by Entry for Event Log Profile  | **11.3**  |

**ANNEX L**

(*Clause* 11.3.4)

## DESCRIPTIVE NOTES ON PROFILE GENERIC INTERFACE CLASS

**L-1** Profile generic objects are available to capture values of attributes from other objects periodically or occasionally. They can be used:

a) for load profiles;

b) for historical; data

c) for event logs, etc.

**L-1.1** The list of attributes to capture is held by the capture object attribute. The values captured are held in the buffer attribute.

**L-1.2** The buffer can be seen as a table, with the capture objects as column headers and a new line of values added with each capture. The data in the buffer can be accessed in its entirety or selectively, using appropriate selection criteria.

**L-1.3** Profile generic objects provide attributes and methods for controlling and managing how data are captured and accessed as illustrated in Fig. 3.

0003

01 00 00 06 00 FF

02

00

0003

01 00 00 06 01 FF

02

00

0008

00 00 01 00 00 FF

02

00

**IC**

**OBIS**

**Attr ID**

**Data index**

X2

X1

Y1

01-01-07 06:00:00

Y2

01-01-07 06:15:00

**.**

**.**

**.**

**.**

**.**

**.**

X16

Y16

01-01-07 10:00:00

15 mnts

Default

16

1000

FIFO

1.0.99.1.0.255

Logical Name

Buffer

Capture Objects

Capture period

Sort method

Sort object

Entries in use

Profile entries

 Fig 3 ILLUSTRATION OF A PROFILE GENERIC OBJECT CONTAINING 16 CAPTURES OF 3 ATTRIBUTES

**L-2 SELECTIVE ACCESS**

There are two types of selective access which allows reading the buffer selectively.

**L-2.1 Selective Access by Entry**

Selective Access by Entry provides a set of 4 integers to filter the contents of the “buffer” attribute in response to get requests as illustrated in Fig. 4. The 4 integers are as below:

a) *From-Entry*- The index of the first entry to return from the buffer.

b) *To-Entry*- The index of the last entry to return from the buffer.

c) *From*-*Value*- The index of the first column to return.

d) *To-Value*- The index of the last column to return.

Thus, the selective access parameters as above can be used to select a subset of the rows from the buffer table.

Also, the selective access parameters as above can be used to select not only a subset of the rows from the buffer table but also a subset of the columns from among the selected rows. Refer to the illustration in Fig. 5. However, this mechanism does not permit retrieving discontinuous ranges of columns from the buffer.

ENTRY\_DESCRIPTOR **{**

00000002

 00000004

 0000

 0000

**}**

01-01-07 06:30:00

Y2

01-01-07 06:15:00

Y3

Y4

01-01-07 06:45:00

Entry 2

Entry 4

Value 2

Value 1

NOTE — This illustration requests from 2nd row to the 4th row.

Fig 4 ILLUSTRATION OF SELECTIVE ACCESS OF PROFILE BUFFER BY ENTRY.



NOTE — This illustration requests only the 2nd and 3rd columns of data from the 2nd row to the 4th row.

FIG. 5 ILLUSTRATION OF SELECTIVE ACCESS OF PROFILE BUFFER BY

ENTRY

**L-2.2 Selective Access by Range**

Selective access by range permits a client to retrieve a subset of the rows and columns in the Profile buffer based on the value of one of the capture objects. Typically, the capture object selected for this purpose is the Clock’s date-time attribute, which is usually one of the capture objects in most profiles as illustrated in Fig. 6. The selective access parameters in this case are as below.

**L-2.2.1** *Restricting object*

 This parameter identifies the capture object whose value will be used to filter the buffer. The object is defined by the OBIS code and attribute index of the selected object.

**L-2.2.2** *From-Value*

The start-range value for the subset. All selected rows in the buffer will have a value for the restricted object that is higher than or equal to this limit.

**L-2.2.3** *To-Value*

The stop-range value for the subset. All selected rows in the buffer will have a value for the restricting object that is lower than or equal to this limit.

**L-2.2.4** *Selected-Values*

An array of column indices specifying the columns that should be returned from the selected rows.

RANGE\_DESCRIPTOR{

 {0008, 0000010000FF, 02, 0000}

 1-1-7 06:00:00

 1-1-7 08:00:00

 00 }

X2

X1

Y1

01-01-07 06:00:00

Y2

01-01-07 06:15:00

**.**

**.**

**.**

**.**

**.**

**.**

X8

Y8

01-01-07 08:00:00

All columns

 are returned

FIG. 6 ILLUSTRATION OF SELECTIVE ACCESS OF PROFILE BUFFER BY

 RANGE

**ANNEX M**

(Foreword)

**ACRONYMS AND ABBREVIATIONS**

|  |  |
| --- | --- |
| *Acronyms and Abbreviation* | *Description* |
|  |  |
| IEC | International Electro-technical Commission |
| NIST | National Institute for Standards and Technology |
| IETF DLMS DLMS UA  COSEM | Internet Engineering Task ForceDevice Language Message SpecificationDevice Language Message Specification User AssociationCompanion Specification for Energy Metering |
| HHU | Hand Held Unit |
| MRI | Meter Reading Instrument |
| DCE | Data Communication Equipment |
| DC | Data Concentrator |
| PSTN | Public Switched Telephone Network |
| GSM | Global System for Mobile Communications |
| GPRS | General Packet Radio Service |
| 802.2 LLC | ISO/ IEC 8802-2 defined Logical Link Control |
| IEEE | Institute of Electrical and Electronics Engineers |
| ASE | Adaptive Server Enterprise for database security |
| ZigBee | Low power wireless connectivity based on IEEE standard 802.15.4 protocol. |
| VZ | Vorwarts Zaehler (previous value counter) |
| IP | Internet Protocol |
| PC | Public Client |
| MR | Meter Reader |
| US | Utility Settings |
| TCP | Transmission Control Protocol (for connection-oriented service) |
| UDP | User Datagram Protocol (for connectionless service) |
|  RS232 / RS485 | Recommended industrial Standards for communication between driver and receiver equipment. |
| TOU | Time of Use |
| ABT | Availability Based Tariff |
| CTTTZ | Conformance Test ToolTime Zone |

**ANNEX N**

(*Foreword*)

**COMMITTEE COMPOSTION**

Equipment for Electrical Energy Measurement, Tariff and Load Control Sectional Committee, ETD 13

*Organization Representative*(*s*)

In personal capacity (Triparna 28/10/1C, Nakuleshwar Bhattachrya, SHRI SUBRATA BISWAS (**Chairman**)

Kalighat, Kolkata)

Areva T&D India Ltd (ALSTOM), Kolkata SHRI H. RAY

Bharat Heavy Electricals Ltd, Bangalore SHRI THARAK RAJ

 SHRI BALASUBRAMANIAN M. (*Alternate*)

Brihan Mumbai Electric Supply & Transport Undertaking, Mumbai SHRI N. V. BHANDAR

 SHRI S. M. SAKPAL (*Alternate*)

BSES Rajdhani Power Ltd, New Delhi SHRI BANSAL RAJESH

 SHRI GITAY RAJ (*Alternate*)

Bureau of Energy Efficiency, New Delhi SHRI G. PANDIAN

CG Actaris Electricity Management Ltd, New Delhi SHRI ASHOK DASH

 SHRI ASHISH TANDON (*Alternate* I)

 SHRI NEELABHRA PAUL (*Alternate* II)

Central Board of Irrigation & Power, New Delhi SHRI K. P. SINGH

 SHRI S. K. BATRA (*Alternate*)

Central Electricity Authority, New Delhi SHRIMATI ANJALI CHANDRA

 SHRIMATI A. K. RAJPUT (*Alternate*)

Central Power Research Institute, Bangalore SHRI R. K. HEGDE

 SHRI B. A. SAWALE (*Alternate*)

CESC Limited, Kolkata SHRI UDAYAN GANGULI

 SHRI SIDDHARTHA MUKHERJEE (*Alternate*)

Development Commissioner Micro, Small & Enterprises, SHRI A. K. VERMA

New Delhi

ECE Industries Ltd, Hyderabad SHRI K. K. SHARMA

Electrical Research & Development Association, Vadodara SHRI U. C. TRIVEDI

 SHRI H. K. MISHRA (*Alternate*)

Elster Metering Private Ltd, Mumbai SHRIMATI MANJUSHRI

Genus Overseas Electronics Ltd, Jaipur SHRI UMESH SONI

Genus Power Infrastructures Ltd, Jaipur SHRI ARVIND KAUL

HPL-Socomec Pvt Ltd, Gurgaon SHRI C. P. JAIN

 SHRI SUNDEEP TANDON (*Alternate*)

IEEMA, New Delhi SHRI SUNIL SINGHVI

 SHRIMATI ANITA GUPTA (*Alternate*)

Jaipur Vidyut Vitaran Nigam Ltd, Jaipur SHRI ARJUN SINGH

Larsen & Toubro Ltd, Mysore SHRI R. M. BHAKTA

 SHRI AHUJA SANJAY (*Alternate*)

Landis & Gyr Ltd, Kolkata SHRI PRADIP RANJAN DUTT

 SHRI S. PAL (*Alternate* I)

 SHRI ANAND SRIVASTAVA (*Alternate* II)

 SHRI R. DUBEY (*Alternate* III)

Maharashtra State Transco Ltd, Mumbai SHRI SANTOSH N. KATAKWAR

National Physical Laboratory, New Delhi SHRI M. K. MITTAL

 SHRI BISWAS (*Alternate*)

North Delhi Power Ltd, New Delhi SHRI R. K. SINGH

 SHRI DESHMUKH (*Alternate*)

NTPC, Noida SHRIMATI M. S. RADHA

 SHRI HIMANSHU SHEKHAR (*Alternate*)

Power Grid Corporation of India Ltd, New Delhi SHRI V. MITTAL

 MS PUNAM (*Alternate*)

PRAYAS, Secundrabad SHRI SREEKUMAR N.

 SHRI GIRISH SANT (*Alternate*)

Rural Electification Corporation Ltd, New Delhi SHRI DINESH KUMAR

 SHRI P. S. HARIHARAN (*Alternate*)

Secure Meters Ltd, Gurgaon SHRI KAUSHIK GHOSH

 SHRI JHALORA SURENDRA (*Alternate* I)

 SHRI SINGHVI S. K. (SML) (*Alternate* II)

The Tata Power Co Ltd, Mumbai SHRI S. C. DHAPRE

 SHRI S. G. JOSHI (*Alternate*)

Voluntary Organisation in Interest of Consumer Education, SHRI T. C. KAPOOR

New Delhi SHRI H. WADHWA (*Alternate*)

Yadav Measurements Pvt Ltd, Udaipur SHRI B. M. VYAS

 SHRI N. K. BHATI N.K (*Alternate*)

BIS Directorate General SHIR R. K. TREHAN, Scientist ‘E’ and Head(ETD)

 [Representing Director General (*Ex-officio*)]

*Member Secretary*

SHRIMATI MANJU GUPTA

Scientist ‘E’ (ETD), BIS

Panel on Metering Protocols and Interoperability, ETD 13/P1

Central Power Research Institute, Bangalore SHRI V. ARUNACHALAM (***Convener***)

Brihan Mumbai Electric Supply & Transport Undertaking, SHRI S. M. SAKPAL

Mumbai

Central Electricity Authority, New Delhi SHRI ALOK GUPTA

CESC Limited, Kolkata SHRI UDAYAN GANGULI

Elster Metering Private Ltd, Mumbai SHRI P. C. KARNIK

HPL-Socomec Pvt Ltd, Gurgaon SHRI C. P. JAIN

Larsen & Toubro Ltd, Mysore SHRI SANJAY AHUJA

Landis & Gyr. Ltd, Kolkata SHRI RAMESHWAR DUBEY

IEEMA, New Delhi SHRI J. PANDE

Kalki Communication Technologies Ltd, Bangalore SHRI VINOO S. WARRIOR

North Delhi Power Ltd, New Delhi SHRI R. K. SINGH

Secure Meters Ltd, Gurgaon SHRI JHALORA SURENDRA

In personal capacity (*Triparna 28/10/1C, Nakuleshwar Bhattachrya,* SHRI SUBRATA BISWAS

*Kalighat, Kolkata*)

(*Continued from second cover*)

India, may be referenced as IEC pre-standards. Contact details of these members can be found at -http://www.dlms.com/organization/listofmembers/index.html.

While writing this Specification it has been endeavoured not to contradict on principle IEC 62056 and the DLMS/COSEM updates on which it is based. However, in case of any divergence/disparity, not amounting to conflict of interpretations that may be revealed later, provisions of this specification will prevail.

The acronyms and abbreviations used in this standard are given in Annex M (*see also* IS/IEC/TR 62051-1).

The composition of the Committee responsible for the formulation of this standard is given at Annex N.

For the purpose of deciding whether a particular requirement of this standard is complied with, the final value, observed or calculated, expressing the result of a test or analysis, shall be rounded off in accordance with IS 2 : 1960 ‘Rules for rounding off numerical values (*revised*)’. The number of significant places retained in the rounded off value should be the same as that of the specified value in this standard.

**Bureau of Indian Standards**

BIS is a statutory institution established under the *Bureau of Indian Standards Act*, 1986 to promote harmonious development of the activities of standardization, marking and quality certification of goods and attending to connected matters in the country.

**Copyright**

BIS has the copyright of all its publications. No part of these publications may be reproduced in any form without the prior permission in writing of BIS. This does not preclude the free use, in the course of implementing the standard, of necessary details, such as symbols and sizes, type or grade designations. Enquiries relating to copyright be addressed to the Director (Publications), BIS.

**Review of Indian Standards**

Amendments are issued to standards as the need arises on the basis of comments. Standards are also reviewed periodically; a standard along with amendments is reaffirmed when such review indicates that no changes are needed; if the review indicates that changes are needed, it is taken up for revision. Users of Indian Standards should ascertain that they are in possession of the latest amendments or edition by referring to the latest issue of ‘BIS Catalogue’ and ‘Standards : Monthly Additions’.

This Indian Standard has been developed from Doc No.: ETD 13 (6211).

**Amendments Issued Since Publication**

|  |
| --- |
| Amend No. Date of Issue Text Affected |
|  |
|  |
|  |
|  |

 BUREAU OF INDIAN STANDARDS

**Headquarters:**

Manak Bhavan, 9 Bahadur Shah Zafar Marg, New Delhi 110002

*Telephones* : 2323 0131, 2323 3375, 2323 9402 *Website*: www.bis.org.in

**Regional Offices:*****Telephones***

Central : Manak Bhavan, 9 Bahadur Shah Zafar Marg 2323 7617

NEW DELHI 110002 2323 3841

Eastern : 1/14 C.I.T. Scheme VII M, 2337 8561

V. I. P. Road, Kankurgachi 2337 8499,

KOLKATA 700054 2337 8626,

 2337 9120

Northern : SCO 335-336, Sector 34-A, 60 3843

CHANDIGARH 160022 60 9285

Southern : C.I.T. Campus, IV Cross Road,

CHENNAI 600113z 2254 1216,

 2254 1442

 2254 2519,

 2254 2315

Western : Manakalaya, E9 MIDC, Marol, Andheri (East)

MUMBAI 400093 2832 9295,

 2832 7858

 2832 7891,

 2832 7892

**Branches:** AHMEDABAD. BANGALORE. BHOPAL. BHUBANESHWAR. COIMBATORE. DEHRADUN. FARIDABAD. GHAZIABAD. GUWAHATI. HYDERABAD. JAIPUR. KANPUR. LUCKNOW. NAGPUR. PARWANOO. PATNA. PUNE. RAJKOT. THIRUVANANTHAPURAM. VISAKHAPATNAM.