Working Draft

Fixing Devices In Walls, Ceilings And Floors Of Solid Construction

Part 2 Design Of Post-Installed

Anchorage To Concrete - Code Of Practice

FOREWORD

(Formal clauses of the standard to be added later)

Various fastening techniques are used extensively for the transfer of loads into concrete structural elements.  One such technique that is, post-installed anchors, installed in hardened structural concrete elements, has become quite common in the last two decades in India.  Despite the extensive use of post-installed anchors in construction, the level of adequate knowledge regarding their behaviour is only increasing now.

Failure of connections poses risk to human life and considerable economic consequences.  Hence, they should be designed, assessed and evaluated in accordance with the well-established engineering principles.  Suitable guidance is therefore required for proper design of such system to ensure safety and reliability.

This standard has, therefore, been formulated to fulfill the above requirements.  It addresses a variety of loading types and failure modes and takes into account the current state-of-the-art for post-installed anchorages in new concrete construction as well as for their use in the repair and strengthening of existing concrete structures.  This standard would provide thus the requisite guidance regarding design and use of anchorages to concrete and would be of help to the designers, contractors and users alike.

In this standard, it has been assumed that the design of anchorages is entrusted to a qualified engineer and that the installation of anchorages to concrete is carried out under the direction of a qualified and experienced supervisor.

In the formulation of this standard, assistance has been derived from the following publications:

- EN 1992-4 : 2018, Eurocode 2 - Design of concrete structures - Part 4: Design of fastenings for use in concrete

- AS 5216 : 2018 Design of post-installed and cast-in fastenings in concrete, Standards Association of Australia

- CEB-FIP Model Code 2011, Design of anchorages in concrete

An informative annex (see Annex C) on general requirements of installation and inspection of anchors to be adopted on the site has been included.

For the purpose of deciding whether a particular requirement of this standard is complied with, the final value, observed or calculated, expressing the result of a test or analysis shall he rounded off in accordance with IS 2: 2022 'Rules for rounding off numerical values (revised)'. The number of significant places retained in the rounded off value should be the same as that of the specified value in this standard.

The standard will be developed in 5 different parts as follows and other parts shall be added with subsequent development –

- Part 1 Devices Other Than Post-Installed Anchors - Code of Practice

- Part 2 Design Of Post-Installed Anchorage To Concrete - Code Of Practice

- Part 3 Testing and Assessment Of Post-Installed Adhesive Anchoring Systems

- Part 4 Testing and Assessment of Post-Installed Mechanical Anchoring Systems

- Part 5 Post-Installed Anchorage to Concrete -Installation and On-site Inspection – Code of Practice

Working Draft

Fixing Devices In Walls, Ceilings And Floors Of Solid Construction

Part 2 Design Of Post-Installed

Anchorage To Concrete - Code Of Practice

1 SCOPE

1.1 This standard deals with the design of post-installed mechanical anchors and post-

installed adhesive anchors in concrete when subjected to static, quasi-static or earthquake loads.  The design method in this standard is applicable only to anchors that have been tested and assessed according to IS 1946 Part 3 and IS 1946 Part 4.  The assessment report (AR) of the anchor generated based on this assessment shall be referred to for various design parameters.  The concrete that forms the base material for the connection shall be in conformity with IS 456 and IS 1343.

1.2 The design provisions in the standard do not apply to cast-in anchors and to anchors in plastic hinge area.

1.3 Specialist literature of eminence may be consulted for guidance regarding fire, fatigue, or blast loads, where applicable.

Note - Specialist literature of eminence refers to any standard (national/ international) beyond the said standard.

2 REFERENCES

The standards (and documents) given in Annex B contain provisions which, through reference in this text, constitute provisions of this standard.  At the time of publication, the editions indicated were valid.  All standards are subject to revision, and parties to agreements based on these standards are encouraged to investigate the possibility of applying the most recent editions of the standards given in Annex B.

3 TERMINOLOGY

For the purpose of this standard, the definition of terms given below shall apply unless otherwise stated.

3.1 Adhesive ― It is a bonding material which is used in adhesive anchor systems.

3.2 Anchor – Steel element, either cast into concrete or post-installed into suitable base material, used to transmit the applied loads.

3.3 Anchorage or Anchoring System – It is an assembly of anchor or anchor group, fixture, and base material (example concrete) surrounding each anchor in which it is installed.

3.4 Anchor Displacement – Movement of the loaded end of the anchor relative to the concrete member into which it is installed, in the direction of the applied load.

3.5 Anchor Group – A number of anchors with identical dimension and characteristics acting together to support a common attachment.

3.6 Annular gap – Gap between the fastening element and concrete when embedded.

FIG. 1 ANNULAR GAP

3.7 Assessment report (AR) – Assessment report of a product (in this case post- installed anchor) is the summary of prequalification of the anchor based on - a transparent and reproducible assessment that complies with the requirement relevant to the - IS 1946 Part 3 and IS 1946 Part 4.

3.8 Base material ― It is the material in which post-installed anchor is installed.

Note: For the given standard, the scope is limited to cast in situ concrete or precast concrete.

  - Base plate – Metal assembly that transmits loads to the anchor.

3.10 Characteristic Value ― It is the value below which not more than 5% of the test results are expected to fall.

FIG. 2 TYPICAL CHARACTERISTIC VALUE

3.11 Concrete

3.11.1 Cracked Concrete – It is concrete where there is probability of formation of cracks after installation of anchor or significant expansion of existing cracks during the service life of the anchors.

3.11.2 Uncracked Concrete – It is concrete where there is no probability of the formation of cracks after installation, or the expansion of any existing crack (like shrinkage crack) is within the permissible limits during the service life of the anchors

3.12 Durability – It is the ability of the anchorage system to contribute during the design service life of the structure under the corresponding service conditions at a performance level compatible with the structural requirements.

3.13 Edge distance – Distance from the center of the anchor perpendicular to the respective edge of the concrete member (Refer Figure 3).

3.13.1 Characteristic Edge Distance – It is the edge distance of an anchor from the face of concrete at which there is no influence of edge on its characteristic strength (Refer Figure 3).

3.13.2 Minimum Edge Distance – It is the minimum edge distance at which the anchor can be installed without damaging the concrete member (Refer Figure 3).

NOTE – The characteristic edge distance is reflected in as the actual projected concrete cone area of the anchorage at the concrete surface. The characteristic dimension is representative of the idealized condition where presence of concrete edges or adjacent anchors does not influence the resistance of an anchor in a group.

Minimum edge distance is the minimum dimension needed to ensure the concrete is not damaged during installation. This minimum edge distance is less than the critical dimension. In such cases, the influence of limited concrete edge reduces the resistance of an anchor in a group.

FIG. 3 CRITICAL AND MINIMUM EDGE DISTANCE

3.14 Embedment depth

3.14.1 Effective embedment (hef) – It is the effective depth which actually transfers the forces passing through the anchor into the concrete.

3.14.2 Nominal embedment – It is the depth at which the bottom of the anchor rests in the drilled hole of the concrete.

Note – The nominal embedment depth may be same as the effective embedment depth for adhesive anchors, however reference may be made to the AR of the specific anchor for exact details.

FIG. 4 EFFECTIVE AND NOMINAL EMBEDMENT DEPTH

3.15 Hole Clearance – Gap in the base plate between the anchor and plate.

FIG. 5 HOLE CLEARANCE

3.16 Mechanical Interlock – It is a load transfer mechanism in which the load is transferred to a concrete member via interlocking surfaces.

3.17 Prying force – It is the additional tensile force which is developed in the anchors due to deformation of the base plate and deformation of anchors.

3.18 Reference Expansion – It is the expansion achieved by applying specified expansion energy.

3.19 Spacing – It is the center to center distance between the anchors (Refer Figure 3).

3.19.1 Characteristic Spacing – It is the spacing between anchors at which there is no influence of spacing on its characteristic strength (Refer Figure 3).

3.19.2 Minimum Spacing – It is the minimum spacing at which the anchor can be installed without damaging the base material (Refer Figure 3).

NOTE – The critical spacing is reflected in as the actual projected concrete cone area of the anchorage at the concrete surface. The critical dimension is representative of the idealized condition where presence of adjacent anchors does not influence the strength of an anchor in a group.

Minimum spacing is the minimum dimension needed to ensure the concrete is not damaged during installation. This minimum spacing is less than the critical dimension. In such cases, the presence of adjacent anchors reduces the resistance of an anchor in a group.

3.20 Stretch Length – It is the length of the anchor that extends beyond concrete surface in which it is anchored.

4 SYMBOLS AND NOTATIONS

For the purpose of this standard, the following letter symbols shall have the meaning indicated against each; where other symbols are used, they are explained at the appropriate place.

4.1 Suffixes

a	― 	Anchor

c	― 	Concrete

cp	― 	Concrete pry-out

cr	― 	Characteristic

cr’	― 	Cracked

d	― 	Design value

g	― 	Group

H	― 	Horizontal

i	― 	Individual

inst	― 	Installation

L	― 	Load

M	― 	Material

m	― 	Mean

mod	― 	modified

p	― 	Pull-out / Pull-through

red	― 	Reduced

Rk	― 	Characteristic value

s	― 	Steel

seis	― 	Seismic/ earthquake

sp	― 	Splitting

u	― 	Ultimate

uncr’	― 	Uncracked

V	― 	Vertical

y	― 	Yield

σ*	― 	Most stressed

0	― 	Basic or idealized

X	― 	In direction X

Y	― 	In direction Y

4.2 Symbols and Notations

| A | ― | Area |
| --- | --- | --- |
| As Es Ec | ― - | Stressed cross section area of steel Modulus of elasticity of steel Modulus of elasticity of concrete |
| c' | ― | Distance from the center of the anchor perpendicular to the respective edge of the concrete member |
| c'1 | ― | Distance of anchor from its center to edge in direction 1; c’1 is the edge distance in direction of the shear load for anchorages close to an edge loaded in shear |
| c'2 | ― | Distance of anchor from its center to edge in direction 2; direction 2 is perpendicular to direction 1 |
| c'cr,N | ― | Characteristic edge distance of an anchor for concrete cone failure |
| c'cr,Np | ― | Characteristic edge distance of an anchor for bond / pull-out failure. |
| c'cr,sp | ― | Characteristic edge distance of an anchor for splitting failure |
| c'min | ― | Minimum edge distance of an anchor |
| da | ― | Anchor diameter of anchor bolt or thread diameter (in case of internally threaded sockets outside diameter of socket) |
| D | ― | concrete member or base material thickness |
| dfix | ― | Diameter of clearance hole in base plate |
| Dmin | ― | Minimum thickness of concrete member in which the anchor can be installed without damaging the concrete member |
| dnom | ― | Outside diameter of anchor |
| d0 | ― | Drill hole diameter |
| eN | ― | Eccentricity of the resulting tensile load acting on the tensioned anchors w.r.t center of gravity |
| eV | ― | Eccentricity of the resulting shear load acting on the anchors w.r.t center of gravity |
| F | ― | Force |
| fck | ― | Characteristic cube compression strength of concrete (measured on cube with side length of 150 mm) |
| fy | ― | Yield strength of steel |
| fu | ― | Ultimate tensile stress for steel |
| Fk,sp | ― | Splitting force |
| hef | ― | Effective anchorage/ embedment depth |
| Ip | ― | Radial moment of inertia |
| M | ― | Moment |
| N | ― | Normal force; positive in tension, negative in compression |
| n | ― | Number of anchors in an anchor group |
| NLd,σ* | ― | Design load on most stressed anchor of group |
| R | ― | Strength or resistance |
| s' | ― | Spacing of anchor in an anchor group |
| s'1 | ― | Centre-to-center spacing of anchors in an anchor group in direction 1 |
| s'2 | ― | Centre-to-center spacing of anchors in an anchor group in direction 2 |
| s'cr,N | ― | Characteristic spacing between anchors for concrete cone failure |
| s'cr,Np | ― | Characteristic spacing between anchors for bond pullout failure |
| s'cr,sp | ― | Characteristic spacing between anchors for splitting failure |
| s'min | ― | Minimum spacing between anchors |
| T | ― | Torsion |
| V | ― | Shear force |
| Zel | ― | Elastic section modulus of anchor calculated from the stressed cross section of steel (πd3 / 32) |
| τ | ― | Bond strength |
| sL | ― | Stress (taken as positive, if tension) in the concrete induced by external loads, including anchors loads |
| sR | ― | Stress (taken as positive, if tension) in the concrete due to restraint of intrinsic imposed deformations or extrinsic imposed deformations |
| αgap | ― | Reduction factor to account for inertia effects due to a gap between anchor and base plate in shear |
| αM | ― | Factor to account for degree of fixity of the anchor |
| αseis | ― | Reduction factor to account for the influence of large cracks and scatter of load-displacement curves under earthquake conditions |
| αV | ― | Angle between shear load on anchors and a line perpendicular to the edge for which the verification for concrete edge failure is being carried out |
| γf | ― | Partial safety factor for load |
| γc | ― | Partial safety factor for concrete |
| γinst | ― | Partial safety factor for installation |
| γM | ― | Partial safety factor for material |
| γMc | ― | Partial safety factor for concrete failure types (cone failure, pull-out /pull-through failure, concrete pry-out failure, concrete edge failure) |
| γMp | ― | Partial safety factor for bond failure |
| γMsp | ― | Partial safety factor for splitting failure |
| γMs | ― | Partial safety factor for steel failure |
| l | ― | Lever arm of shear load |

5 Post-installed Anchor

5.1 General – It is a type of anchor in which the anchor is installed into cured and hardened concrete. It can transfer applied loads through friction, keying, adhesion or a combination of these working principles. (see Fig. 6). Post-installed anchors are broadly divided in two categories – Mechanical anchors and Adhesive anchors.

(6A) LOAD TRANSFER DUE TO FRICTION & KEYING BETWEEN METAL PARTS & CONCRETE.

(6B) LOAD TRANSFER DUE TO MECHANICAL INETRLOCK (BEARING) BETWEEN METAL PART & CONCRETE.

(6C) LOAD TRANSFER DUE TO BOND BETWEEN METAL PARTS & ADHESIVE AND BETWEEN CONCRETE & ADHESIVE

FIG. 6 TYPICAL LOAD TRANSFER MECHANISM OF POST-INSTALLED ANCHORS

##### 5.2 TYPES OF POST-INSTALLED ANCHOR

5.2.1 Adhesive Anchor – It is a type of post-installed anchor. The adhesive anchors consist of threaded anchor rods or reinforcement bars, which are anchored in pre-drilled holes in hardened concrete by bonding the metal parts of the anchor/reinforcement to the sides of the drilled hole with an adhesive. The adhesives used comprise of chemical components formulated from organic polymers (like, epoxies, polyurethanes, etc.) orinorganic materials (usually cementitious) that hardens on curing. Tensile loads are transmitted to the concrete through bonding between metal parts and adhesive, and between adhesive and concrete face of the drilled hole (See Fig. 7).

Note: While deciding the use of adhesives, comprised particularly of organic polymers, their temperature range is needed to be accounted for as per the temperature of the base material at the time of installation and expected application during its service life.

FIG. 7 ADHESIVE ANCHOR

5.2.1.1 Special type of adhesive anchor

- Torque-controlled Adhesive Anchor – It is a type of adhesive anchor designed such that its outward/ upward movement relative to the hardened adhesive compound results in a follow-up expansion of the adhesive. The working principle is triggered by application of torque (see Fig. 8)

FIG. 8 TYPICAL TORQUE-CONTROLLED ADHESIVE ANCHOR

- Undercut Adhesive Anchor – It is a type of adhesive anchor. It combines the undercut concept of mechanical anchor with bonding mechanism of adhesive anchor (see Fig. 9).

FIG. 9 TYPICAL UNDERCUT ADHESIVE ANCHOR

5.2.1.2 Adhesive Anchor Types based on dispensing technique – Adhesive anchor systems are classified into bulk, capsule type and cartridge type adhesive anchoring systems.

- Bulk Adhesive Anchor System – This is one of the systems for large application for installing adhesive anchors. This system comprises of two-component adhesive (resin and hardener) that are supplied either in barrels or cans. These incorporate bulk dispensing and mixing machine whereby preset quantities of the components are automatically controlled during dispensing (see Fig. 10).

FIG. 10 TYPICAL BULK ADHESIVE SYSTEM

- Capsule Adhesive Anchor System – This is one of the systems of installing adhesive anchors. In this system, the adhesive is packaged in glass or foil capsules. The diameter of capsule corresponds approximately to nominal anchor diameter. The quantity of resin and hardener in each capsule is such that it is suitable for single anchor application. Mixing of various components in each capsule is achieved during anchor installation process. The capsule gets fragmented, and it becomes part of the hardened resin matrix during anchor installation process (see Fig. 11).

FIG. 11 TYPICAL CAPSULE ADHESIVE SYSTEM

- Cartridge Adhesive Anchor System –This is one of the systems of installing adhesive anchors. In this system, two-component adhesives (resin and hardener) are packaged in cartridges for use with either manually- or power-driven dispensers. Metering and mixing of the components is automatically controlled as the adhesive is dispensed through a manifold and disposable mixing nozzle (see Fig. 12).

FIG. 12 TYPICAL CARTRIDGE ADHESIVE SYSTEM

5.2.2 Mechanical Anchor – It is a type of post-installed anchor i.e. anchor installed after casting and hardening of concrete. Mechanical anchors typically transfer load to concrete through friction, keying, mechanical interlocking, or combination of any of these three working principles. The post- installed mechanical anchoring systems are further subdivided into three categories – concrete screws, expansion anchors and undercut anchors, depending on their working principles.

5.2.2.1 Concrete Screw – It is a type of post-installed anchor with threads that are screwed into a predrilled hole where threads create a mechanical interlock with the concrete (see Fig. 13)

FIG.13 TYPICAL CONCRETE SCREW

5.2.2.2 Expansion Anchors – Expansion anchors are a type of post-installed mechanical anchor. They are anchored in predrilled holes in hardened concrete by forced expansion of sleeve. A tensile force applied to the anchor is transferred to the concrete by friction and some keying between an expanded sleeve and the concrete. Expansion anchors can be broadly classified into two types - Displacement-controlled expansion anchor [Fig. 14(a)] and Torque-controlled expansion anchor [Fig. 14(b)].

| (14A) EXAMPLE OF DISPLACEMENT-CONTROLLED EXPANSION ANCHOR | (14B) EXAMPLE OF TORQUE-CONTROLLED EXPANSION ANCHOR |
| --- | --- |

FIG. 14 DIFFERENT TYPES OF EXPANSION ANCHORS.

(a) Displacement-controlled Expansion Anchor ― It is a type of mechanical expansion anchor.  It is set by expansion against the sides of the drilled hole through movement of an internal plug in the sleeve or through movement of the sleeve over an expansion element (like plug). This is achieved by driving through hammer blows or by percussion of a machine.  Once set, no further expansion can occur.  Displacement-controlled expansion anchors are installed by hammer blows or by percussion of a machine.  In some types of displacement-controlled expansion anchors, the sleeve is expanded by driving in a cone; the extent of expansion in this case is controlled by the length of travel of the cone [Fig. 15(a)].  In other types, the sleeve is driven over an expansion element, wherein the extent of expansion is controlled by the travel of the sleeve over the expansion element [Fig. 15(b)].  The expansion forces created during anchor installation along with tension forces are transferred into the concrete mainly by friction. Some of the common types of displacement-controlled expansion anchors are – Cone down type anchor like drop-in anchor [Fig. 15(c)], sleeve-down type anchor [Fig. 15(d)] and Stud version of sleeve-down type anchor [Fig. 15(e)].

(15A) EXPANSION BEING CONTROLLED BY LENGTH OF TRAVEL OF THE CONE.

##### (15B) EXAMPLE OF DISPLACEMENT-CONTROLLED EXPANSION ANCHOR

##### EXPANSION BEING CONTROLLED BY LENGTH OF TRAVEL OF THE SLEEVE.

(15C) CONE-DOWN TYPE ANCHOR.

(15D) SLEEVE-DOWN TYPE ANCHOR DRILLING CONTROLLED BY STOP-DRILL BIT.

(15E) STUD VERSION OF SLEEVE-DOWN TYPE ANCHOR.

FIG.15 DISPLACEMENT-CONTROLLED EXPANSION ANCHORS.

(b) Torque-controlled Expansion Anchor – It is a type of mechanical expansion anchor. It is set by the expansion of one or more sleeves or other elements against the sides of the drilled hole through the application of torque, which pulls the cone(s) into the expansion sleeve(s). Tensile loading can cause additional expansion (follow-up expansion) after setting up of anchor. Some of the common types of torque-controlled expansion anchors are sleeve type expansion anchors with one cone [see Fig.16 (a)] or more than one cone, bolt type expansion anchors with one cone [see Fig. 16 (b)] or more than one cone and combination of sleeve and bolt type.

(16A) SLEEVE TYPE                                    (16B) BOLT TYPE

FIG. 16 TYPICAL TORQUE-CONTROLLED EXPANSION ANCHOR

5.2.2.3 Undercut Anchor – It is a type of mechanical anchor. It is anchored by mechanical (bearing) interlock provided by an undercut in the concrete. It is a type of anchor which derives its strength from mechanical interlock provided by an undercut in the concrete at the embedded end of the anchor. The undercutting in undercut anchors may be achieved by:

- Hammering or turning (or both) the anchor sleeve into a drilled undercut hole.

- Hammering or turning (or both) the anchor sleeve on to the tapered bolt in a cylindrical hole. In this case, the concrete is mostly cut away rather than compressed.

Installation of undercut anchors can be sub-divided into displacement-controlled installations and torque-controlled installations. In case of displacement-controlled installations, the holes are drilled with a stop-drill to ensure correct installation depth for anchors. In case of torque-controlled installations, the expansion is controlled by defined torque moment (see Fig. 17).

(17 A) UNDERCUT ANCHOR THAT REQUIRES UNDERCUT TO BE CREATED PRIOR TO INSTALLATION

(17 B) UNDERCUT ANCHOR THAT DOES NOT REQUIRE UNDERCUT TO BE CREATED PRIOR TO INSTALLATION.

FIG. 17 TYPICAL UNDERCUT (MECHANICAL) ANCHOR

Note: The selection of the appropriate type of anchor shall be governed by multiple factors like condition of the existing concrete, area of application, type of load, magnitude of load, feasibility of application. E.g., in a poorly compacted concrete, for high tension load or for close to the edge applications, adhesive anchors may be preferred. For high shear dominated applications, mechanical anchors may be preferred. However, this is not restrictive in nature as to use of the anchors. The selection may be made by the concerned structural engineer and confirmed by the manufacturer.

Note: Special care must be exercised while designing post-installed anchors in case of fire and the characteristic resistance of the anchor as per the assessment report of the anchor corresponding to the given fire rating shall be referred to. Design of anchor for fire is out of scope of this standard.

6 FAILURE MODES OF POST-INSTALLED ANCHORS

6.1 Bond Failure or Pull-out Failure of adhesive anchors ― It is a failure type observed for adhesive anchors in tension. This failure occurs either at the interface between the adhesive and the base material or between the adhesive and the embedded element (like threaded rod) of the adhesive anchor. This failure is typically accompanied with a shallow concrete cone at the loaded end of anchor. Bond failure is a sub type of pullout failure which is applicable only for adhesive anchors (see Fig. 18).

Note – This is a combined pull-out and cone failure in case of adhesive anchor, referred to as pull-out (bond) failure in this document.

`

(18 A) BOND FAILURE BASE MATERIAL AND ADHESIVE INTERFACE

(18 B) BOND FAILURE AT ADHESIVE AND EMBEDDED ELEMENT INTERFACE

FIG. 18 BOND FAILURE

6.2 Concrete Cone Failure – This failure type is typically observed in both mechanical and adhesive anchors installed at shallow embedment depths under tension loading. This failure mechanism is characterized by the formation of a conical fracture surface originating at or near the embedded end of the anchor element and projecting to the surface of the concrete member. This failure mode is also observed in groups of mechanical and adhesive anchors installed at less than characteristic spacing.  This type of failure can also occur when the anchor is located at a distance less than the characteristic distance (see Fig. 19).

FIG. 19 TYPICAL CONCRETE CONE FAILURE

6.3 Concrete Edge Failure – This failure type is observed for both mechanical and adhesive anchors installed at less than characteristic edge distance under shear loading (with shear acting towards the free edge). (see Fig. 20).

FIG. 20 TYPICAL CONCRETE EDGE FAILURE

6.4 Concrete Pry-out Failure – This failure type is observed for both mechanical and adhesive anchors installed at shallow embedment under shear loading (see Fig. 21). Concrete pry-out failure corresponds to the formation of a concrete spall opposite to the loading direction under shear loading.

FIG. 21 TYPICAL CONCRETE PRY-OUT FAILURE

6.5 Pull-out Failure of Mechanical Anchor – This failure type is observed for mechanical anchors under tension loading. It is characterized by the withdrawal of the anchor element from the concrete without rupture of the embedded part. The formation of limited-depth conical breakout surfaces are also considered as pullout failures (see Fig. 22).

FIG. 22 TYPICAL PULL-OUT FAILURE

6.6 Pull-through Failure of Mechanical Anchor – This failure type is observed for mechanical anchors under tension loading in which the anchor body pulls through the expansion sleeve without development of the full steel or concrete capacity (see Fig. 23).

FIG. 23 TYPICAL PULL-THROUGH FAILURE

6.7 Splitting Failure – This failure type is observed for both mechanical and adhesive anchors installed in a ‘thin’ concrete member under tension loading. It is essentially a concrete failure mode in which the concrete fractures along a plane passing through the axis of the anchor or anchor group (see Fig. 24).

FIG. 24 TYPICAL SPLITTING FAILURE

6.8 Steel Failure – This failure mode is observed for both mechanical and adhesive anchors under tension or shear loading. In this failure type, the steel anchor parts are fractured (see Fig 25).

(25 A) STEEL FAILURE IN TENSION

##### (25 B) STEEL FAILURE IN SHEAR

FIG. 25 TYPICAL STEEL FAILURE

(26A) ANCHOR GROUPS SUBJECTED TO TENSILE LOAD

(26B) ANCHOR GROUPS SUBJECTED TO SHEAR LOAD

FIG. 26 NOTATIONS AND SYMBOLS

7 ANCHORS AND ANCHOR GROUP CONFIGURATIONS

The connection in a structure shall be designed so as to be consistent with the assumptions made in analysis of the structure and comply with requirements specified in this standard.  The connections shall be capable of transmitting the calculated design loads in tension, shear or combined tension and shear. A suitable grouting material of sufficient compressive strength (non-shrink cementitious grout based) shall be provided between the concrete surface and the base plate, if required. The thickness of the grouting material shall be such that it does not create any stand-off between the base material and the plate.

7.1 Anchor

The anchors may be subjected to tension, shear, or combination of both and bending (in case of stand-off).  The anchors are not considered to transfer any compression force. The anchors may be made of suitable materials such as carbon steel, stainless steel or malleable cast iron. The anchors may include non-load bearing material such as plastic parts for rotation prevention.

NOTE: Undercut adhesive anchors are not covered in this standard.

7.2 Anchor Diameter and Embedment

The anchors shall have a minimum diameter of 6 mm.

7.2.1 For mechanical anchors, the embedment depth of the anchor shall be at least 6 times the anchor diameter, but not less than 40 mm. For fastening statically indeterminate non-structural elements, minimum embedment depth of anchor shall be 30 mm.

7.2.2 For adhesive anchors, the maximum embedment depth for design of the anchor shall be 20 times the anchor element diameter. Any embedment depth in excess of 20 times diameter shall be ignored in design calculation.  The minimum embedment depth (hef) shall be as follows:

For

da ≤10 mm, 	hef= 60 mm.

da=12 mm, 	hef=  70 mm;

da =16 mm	, 	hef=  80 mm;

da =20 mm,	hef=  90 mm; and

da ≥24 mm,	hef=  4da .

7.3 Location Details of Anchors

7.3.1 Clearance Holes in Base Plate for Anchors

The diameter of clearance hole (dfix) in the base plate shall not be larger than the values given below with the following exception that for an individual anchor or anchor groups loaded in pure tension, a larger diameter of the clearance hole is acceptable if a suitable washer is used.

For,  d<10 mm 		dfix= d + 1

10 < d < 24 mm 		dfix= d + 2

d > 24mm	 	            dfix= d + 3

d = da, if bolt bears against the base plate d = dnom, if sleeve bears against the base plate

Note – The above dimensions shall not be applicable for concrete screws. For concrete screws, reference shall be made to the AR of the anchor.

7.3.2 Permissible Anchor Group Configurations

The anchor group configurations illustrated in Fig. 27 are valid for all loading directions and all edge distances, provided the gap between anchor and plate is filled during installation.  The gap shall be filled up by a suitable filling material of compatible strength

FIG. 27 ANCHOR GROUP CONFIGURATION WHEN GAPS BETWEEN THE PLATE AND THE ANCHOR ARE FILLED UP FOR ALL EDGE DISTANCE AND FOR ALL LOAD DIRECTIONS (SHEAR FORCE IS TAKEN UP BY ALL ANCHORS)

In case hole filling cannot be ensured at site, the following arrangements are allowed (see Fig. 28).

FIG. 28 ANCHORS WITH HOLE CLEARANCE ACCORDING TO 7.3.1. (WHEN GAPS BETWEEN THE PLATE AND ANCHOR ARE NOT FILLED UP) FOR ALL LOAD DIRECTIONS (SHEAR FORCE IS TAKEN UP BY THE FRONT ROW OF ANCHORS)

NOTE – Other anchor arrangements such as triangular or circular pattern may be allowed; however, the provisions of this standard should be applied with required engineering judgment in such cases.

7.4 Concrete Base Material

The concrete thicknesses required for post-installed mechanical anchors shall be at least 2hef, but not less than 120 mm. The concrete thicknesses required for post-installed adhesive anchors shall be at least equal to (hef + ΔD), but not less than 100 mm,  ΔD shall be taken as 2d0 or 30 mm whichever is larger. Concrete shall be assumed to be cracked for design purpose.

NOTE – In some cases, uncracked concrete may be assumed if under service conditions the anchor with its entire anchorage depth is located in compression zone. This will be satisfied if the following equation is observed.

sL + sR≤ 0

where, sL= Stress (taken as positive, if tension) in the concrete induced by external loads, including anchors loads.

sR = Stress (taken as positive, if tension) in the concrete due to restraint of intrinsic imposed deformations or extrinsic imposed deformations such as displacement of support and temperature variations. (see IS 456).

8 STRUCTURAL ANALYSIS

Loads and moments acting on the anchorage shall be determined using general principles of structural analysis (elastic) taking into account partial safety factors.

8.1 Tension Load – The direct tension forces and bending moments acting on the base plate shall be resolved into tension load acting on each anchor and shall be calculated according to the theory of elasticity using the following assumptions:

a) The anchor plate shall not deform under the design loads.

NOTE – For this assumption to be valid, the anchor plate shall be sufficiently stiff. Guidance may be taken from IS 800 on steel plate design.

b) The axial stiffness (EsAs) of all anchors shall be equal, where Es shall be taken as per structural properties of material of the anchor.

c)  The anchors shall not be considered to contribute in the transmission of normal forces in the zone of compression under the base plate. The compression forces shall be assumed to be transferred to concrete through the grout layer, if present.

d) The modulus of elasticity of concrete (Ec) shall be considered as per IS 456.

If the magnitude of tension force acting on individual anchors (NL,i) of an anchor group is different, then the eccentricity eN of the total tension force acting on the anchor group (NL,g) shall be calculated to enable accurate assessment of strength of the anchor group (see Fig. 29).

NOTE – Prying forces may occur due to deformation of base plates and displacement of anchors and shall be taken into account.  Prying forces are avoided using rigid base plates.

(29A) ECCENTRICITY IN ONE DIRECTION WHEN ALL ANCHORS ARE IN TENSION

(29B) ECCENTRICITY IN ONE DIRECTION WHEN ONLY SOME OF THE ANCHORS OF AN ANCHOR GROUP ARE LOADED IN TENSION

(29C) ECCENTRICITY IN TWO DIRECTIONS WHEN ONLY SOME OF THE ANCHORS OF AN ANCHOR GROUP ARE LOADED IN TENSION

(29D) ANCHORAGE LOADED BY A BENDING MOMENT AND TENSION FORCE

FIG. 29 TYPICAL ANCHOR GROUPS SUBJECTED TO ECCENTRIC LOAD

8.2 Shear Load

8.2.1 Distribution of Shear Loads

The distribution of shear loads is dependent on the effectiveness of the anchors to resist shear loads which is influenced by the hole clearance and the edge distance.

a) In case of steel failure and concrete pry-out failure, it shall be assumed that all anchors of an anchor group will take up shear load (see Fig. 30).

(30A) ANCHOR TAKING SHEAR LOAD                   (30B) TWO ANCHORS SUBJECTED TO SHEAR SUBJECTED TO SHEAR AND MOMENT

(30C) MULTIPLE ANCHORS SUBJECTED TO SHEAR

FIG. 30 EXAMPLE OF LOAD DISTRIBUTION FOR CASES WHEN ALL ANCHORS TAKE UP SHEAR LOAD

b) In case of concrete edge failure and filled clearance holes between the anchor and the base plate, it shall be assumed that all anchors take up shear forces perpendicular and parallel to the edge (see Fig. 31).

(31A) TWO ANCHOR GROUP                        (31B)   FOUR ANCHOR GROUP

FIG. 31 EXAMPLE OF DISTRIBUTION OF SHEAR LOAD - ANCHOR LOCATED NEAR THE EDGE (WHEN GAP BETWEEN THE ANCHOR AND THE BASE PLATE IS FILLED UP)

c) In case of concrete edge failure with an unfilled clearance hole according to 7.3.1, it shall be assumed that only the most unfavorable anchor (first row of anchor) will take up shear loads acting perpendicular towards the edge (see Fig. 32).  In case the shear is acting parallel to the edge then all anchors shall be assumed to take up shear load

NOTE ─ The slotted holes in base plates in the direction of shear load prevent anchors from taking up shear loads and may be used in case of fastenings close to an edge (see Fig. 33). In this case, the anchors near to the edge would not take shear but other anchors can be designed for their full capacity.

For, eccentrically loaded connections, shear load transfer shall follow similar principles as above and load distribution shall be in accordance with Fig. 34.

(32A)         					         (32B)

FIG. 32 EXAMPLE OF DISTRIBUTION OF SHEAR LOAD - ANCHOR LOCATED NEAR THE EDGE (WHEN GAP BETWEEN THE ANCHOR AND THE BASE PLATE IS NOT FILLED UP

FIG. 33 EXAMPLE OF LOAD DISTRIBUTION FOR ANCHORAGE WITH SLOTTED HOLES

FIG. 34 EXAMPLE OF ANCHORAGE SUBJECTED TO ECCENTRIC SHEAR LOAD

8.2.2 Determination of Shear Loads

The direct shear forces and torsion acting on the base plate shall be resolved into shear load acting on each anchor and shall be calculated according to the theory of elasticity assuming equal stiffness for all anchors in an anchor group. Equilibrium shall be satisfied.  Some examples are illustrated in Fig. 34.

(35A) GROUP OF THREE ANCHORS SUBJECTED TO SHEAR

(35B) GROUP OF FOUR ANCHORS SUBJECTED TO SHEAR

(35C) GROUP OF FOUR ANCHORS SUBJECTED TO INCLINED SHEAR

(35D) GROUP OF FOUR ANCHORS SUBJECTED TO TORSION MOMENT

FIG. 35 DETERMINATION OF SHEAR LOADS FOR CASES WHEN LOAD IS TAKEN UP BY ALL ANCHORS, IN CASE OF STEEL AND CONCRETE PRY-OUT FAILURE

In case of anticipated concrete edge failure (that is, when anchors are located close to edge), it shall be assumed that all anchors take up shear forces perpendicular and parallel to the edge, given that the gap between the anchor and base plate is filled up (see Fig. 36).  In case the shear is acting parallel to the edge then all anchors shall be assumed to take up shear load.

(36A) GROUP OF TWO ANCHORS WHEN LOADED IN SHEAR PARALLEL TO THE EDGE

(36B) GROUP OF FOUR ANCHORS WHEN LOADED BY INCLINED SHEAR LOAD

(36C) GROUP OF TWO ANCHORS WHEN LOADED IN SHEAR PERPENDICULAR TO THE EDGE

FIG. 36 DETERMINATION OF SHEAR LOADS FOR CASES WHEN LOAD IS TAKEN UP BY ALL ANCHORS (THAT IS, GAP BETWEENT THE ANCHOR AND THE BASE PLATE IS FILLED UP)

In special cases where the gap between the base plate and the anchor cannot be filled up or in case of seismic shear loading, the anchors located in most unfavorable position (that is anchors located closest to the edge) in case of concrete edge failure shall take up load. In case the shear load is acting parallel to the edge then all anchors shall be assumed to take up shear load. In case of concrete edge failure, if the anchor group is subjected to inclined shear, then the load components acting perpendicular to the edge shall be taken up by the most unfavorable anchors, while the load components acting parallel to the edge shall be equally distributed to all anchors of the group (see Fig. 37).

(37A) GROUP OF TWO ANCHORS WHEN LOADED IN SHEAR PARALLEL TO THE EDGE

(37B) GROUP OF FOUR ANCHORS WHEN LOADED BY INCLINED SHEAR LOAD

(37C) GROUP OF TWO ANCHORS WHEN LOADED IN SHEAR PERPENDICULAR TO THE EDGE

FIG. 37 DETERMINATION OF SHEAR LOADS FOR CASES WHEN LOAD IS TAKEN UP BY EDGE ANCHORS (THAT IS, GAP BETWEEN THE ANCHOR AND THE BASE PLATE IS NOT FILLED UP)

8.2.2.1

Loaded anchor

Unloaded anchor

Edge

VSd

VSd

a) Group of two anchors loaded by a shear load perpendicular to the edge

If the following conditions are met then it shall be assumed that anchors are subjected to shear loads without lever arm:

- The base plate is made of metal.  In the area of the anchorage, the base plate is fixed directly to the concrete either without an intermediate layer or with a leveling layer of mortar with compression strength of at least 30 N/mm2 and thickness < da/2.

- The base plate is in contact with the anchor over its entire thickness.

8.2.2.2 If the conditions given in 8.2.2.1 are not fulfilled then lever arm of shear load (l) shall be calculated according to the following equation (see Fig. 38).

l = a3 + e1												where,

a3 = 0.5da[exception: if a washer and a nut is directly clamped to the 			        concrete surface (see Fig. 38B), then a3 = 0]

e1 = Distance between shear load and concrete surface

(see Fig. 38A and 38B)

da  = Anchor diameter; in case sleeve bears against the base plate use

sleeve diameter (dnom) (see Fig. 38A).

(38A) FOR ANCHORS DRILLED AND GROUTED

(38B) FOR ANCHORS BOLTED ON THE SURFACE

FIG. 38 DETERMINATION OF LEVER ARM

8.2.2.3 The design moment acting on the anchor due to shear load with lever arm shall be calculated according to the following equation:

MLd=VLdlαM

The value αM in this equation depends on the degree of fixity of the anchor at the side of the base plate of the application in question. It shall be judged according to sound engineering practice.

If the base plate can rotate freely (see Fig. 39A), then no fixity (αM = 1.0) shall be assumed.

If the base plate is not free to rotate (see Fig. 39B), then full fixity (αM = 2.0) shall be assumed.

The base plate shall be able to take up the fixing moment in case restraint of the anchor is assumed.

(39A) BASE PLATE WITHOUT ROTATIONAL RESTRAINT (αM= 1.0)

(39B) BASE PLATE WITH ROTATIONAL RESTRAINT (αM= 2.0)

FIG. 39 BASE PLATE RESTRAINT CONDITIONS

9 DESIGN OF POST-INSTALLED ANCHORING SYSTEMS FOR STATIC OR QUASI-STATIC CONDITIONS

9.1 General

The characteristic values of the anchor to be used for the calculation of anchor strength and parameters like spacing, edge distance, minimum thickness of concrete member, etc. shall be taken from the assessment report (AR) of the anchor.

9.1.1 Limit State Design

The design of anchorages shall be done using limit state design method.  It shall be established that the value of the design load, Ld does not exceed the value of the design strength, Rd.

Ld≤Rd

where,

Ld	=	γfLe

Le	=	Unfactored loads shall be obtained from IS 875 (all Parts)

γf	=	Partial safety factor for loads (as per IS 456)

Rd	=	RkγM

Rk	=	Characteristic strength of a single anchor or an anchor group

γM	=	Partial safety factor for material.

9.1.2 Limit State of Strength

The limit state of strength are those associated with failures, under the action of most critical

combination of loads on the anchorages using the appropriate partial safety factors, which may endanger the safety of life and property.

9.1.3 Limit State of Serviceability

In the serviceability limit state, it shall be ensured that the displacements of anchors occurring under the design loads are not larger than the admissible displacement as may be decided by the structural engineer.

NOTE –– The admissible displacement depends on the application in question and shall be decided by the structural designer.

9.1.3.1 Displacements

The characteristic displacement of the anchor under defined tension and shear loads shall be taken from the Assessment Report.  The displacements shall be assumed as a linear function of the applied load.  In the case of combined tension and shear load, the displacements for the tension and the displacement for the shear component of the resultant load shall be geometrically added.  The influence of the hole clearance in the base plate on the expected displacement of the whole anchorage system shall be taken into account in case of shear loads.

9.2 Design Method

The design strength shall be calculated according to limit state method of design for all load directions, namely tension, shear individually or combined as well as for all applicable failure modes. The minimum strength shall govern after verification of interaction of tension and shear forces for the load case.

9.2.1 Partial Safety Factors

a) Partial safety factor for concrete failure

These could be cone failure (γMc), pull-out / pull-through failure (γMp), concrete pry-out failure (γMc), concrete edge failure (γMc), splitting failure (γMsp) and bond failure (γMp).

γMc=γMsp=γMp=γc.γinst

γc = Partial safety factor for concrete (as per IS 456) = 1.5

γinst = Installation safety factor of an anchor system in tension shall be taken from AR of the anchor.  Installation safety factor of an anchor system in shear shall be taken as 1.0.

b) Partial safety factor for Steel failure (γMs)

For tension loading: γMs=1.2fyfu≥1.4

For shear loading of the anchor with and without lever arm:

γMs=1.0fyfu≥1.25  	(for fu≤800  N/mm2 and fyfu≤0.8)

γMs=1.5			(for fu>800  N/mm2 or fyfu>0.8)

9.2.2 Design Strength in Tension

The design strength in tension shall be calculated and checked according to limit state of design for all applicable failure modes as per Table 1, and the minimum strength shall govern.

Table 1 Design Strength Checks in Tension

(Clause 9.2.2)

| Sl No (1) | Strength to Resist Expected Failure Types (2) | Checks for Single Anchor (3) | Checks for Anchor Group (4) |
| --- | --- | --- | --- |
| i) | Steel strength | NLd≤ NRk,sγMs | NLd,σ*≤ NRk,sγMs |
| ii) | Concrete cone strength | NLd≤ NRk,cγMc | NLd,g≤ NRk,cγMc |
| iii) | Pull-out strength of mechanical anchor/ torque controlled adhesive anchor | NLd≤ NRk,pγMp | NLd,σ*≤ NRk,pγMp |
| iv) | Pull-out strength of adhesive anchor | NLd≤ NRk,pγMp | NLd,g≤ NRk,pγMp |
| v) | Splitting strength | NLd≤ NRk,spγMsp | NLd,g≤ NRk,spγMsp |

9.2.2.1 Determination of steel strength

The characteristic steel strength (NRk,s) of an anchor shall be taken from the AR of the anchor and the steel strength check in tension shall be performed according to       Table 1.

NOTE – If the value of characteristic steel strength is not available in the AR then it may be calculated using the following equation, NRk,s=Asfu

9.2.2.2 Determination of concrete cone strength

The characteristic concrete cone strength of an individual anchor or an anchor group, respectively, shall be determined according to the following equation:

NRk,c=NRk,c0Ac,NAc,N0Ψs,NΨre,NΨec,N ΨM,N

where

NRk,c0= The characteristic strength of a single anchor placed in cracked or uncracked concrete in tension not influenced by adjacent anchors or edges of the concrete member

NRk,c0=7.2fckhef1.5 (for applications in cracked concrete)

NRk,c0=10.1fckhef1.5 (for applications in uncracked concrete)

The constants 7.2 and 10.1 are corresponding to fck

s'cr,N=3hef=2c'cr,N

Ψs,N= Factor to account for discontinuities in the symmetric stress distribution in the concrete due to edges of the concrete member. The smallest edge distance shall be used as c’ in the following equation.

Ψs,N=0.7+0.3c'c'cr,N≤1.0

Ψre,N= Factor to account for the effect of dense reinforcement between which the anchor is installed, when hef<100.

Ψre,N=0.5+hef200≤1.0

NOTE – If in the area of the anchorage there is reinforcement with a spacing > 150 mm (any diameter) or with a diameter < 10 mm and a spacing > 100 mm then the factor  Ψre,N shall be taken as 1.0.

Ψec,N= Factor to account for group effect when different tension loads are acting on the individual anchors of an anchor group. Where there is an eccentricity in two directions, Ψec,N shall be determined separately for each direction and the product of both factors shall be inserted the above equation for determining  NRk,c.

Ψec,N=11+2eNs'cr,N≤1

Ac,N0= Idealized projected concrete cone area of an individual anchor with no influence of edge and spacing on the concrete cone strength of the anchor. It shall be calculated by idealizing the concrete cone as a pyramid with a height equal to hef and a base length equal to s'cr,N (see Fig. 40), Ac,N0=s'cr,N∙s'cr,N

Ac,N= Actual projected concrete cone area of the anchorage at the concrete surface.

It is limited by overlapping concrete cones of adjoining anchors as well as by

edges of the concrete member when edge and spacing are less than the characteristic

values. (see Fig. 41).

ΨM,N = Factor to account for the influence of a compression force between the base plate and the concrete on the tensile strength of the anchor in cases of bending moments with or without axial force. The value shall be considered as 1 if either of the following criteria are met:

a) The anchor is located close to the edge c'<1.5 hef

b) Anchors which are located away from the edge (c'>1.5 hef) and loaded by bending moment as well as tension force, satisfy the equation  Nc”NLd    <0.8

c) zhef≥1.5

For all other applications, it should be taken as 2-zhef ≥1

(z = lever arm and Nc” is the resultant compression force between the base plate and the concrete)

For direct tension forces the factor ΨM,N shall be considered as 1.

FIG. 40 IDEALIZED PROJECTED CONCRETE CONE AREA OF AN INDIVIDUAL ANCHOR

Ac,N = (c’1 + 0.5s’cr,N)*s’cr,N

where

c’1 ≤ c’cr,N

c’1 ≤ c’cr,N

(41A) INDIVIDUAL ANCHOR LOCATED CLOSE TO THE EDGE OF CONCRETE MEMBER

Ac,N = (c'1 +s’1+ 0.5s’cr,N)*s’cr,N

where

c'1 ≤ c'cr,N

s’1 ≤ s’cr,N

(41B) GROUP OF TWO ANCHORS LOCATED CLOSE TO THE EDGE OF CONCRETE MEMBER

Ac,N = (c'1 +s’1+ 0.5s’cr,N)*

(c'2 +s’2+ 0.5s’cr,N)

where

c'1 & c'2 ≤ c'cr,N

s’1 & s’2 ≤ s’cr,N

(41C) GROUP OF FOUR ANCHORS LOCATED AT A CORNER OF CONCRETE MEMBER

FIG. 41 EXAMPLES OF ACTUAL PROJECTED CONCRETE CONE AREA FOR DIFFERENT ANCHOR CONFIGURATIONS

9.2.2.2.1 Special Case

For anchorages with three or more edges with the largest edge distance less than the characteristic edge distance for concrete cone in tension (see Fig. 41), the calculation of strength as above may lead to very conservative values. For such cases, the embedment depth,hef, spacing, s'cr,N and edge distance, c'cr,N shall be substituted with their modified values as indicated below for determining the characteristic concrete cone strength, NRk,c  according to 9.2.2.2.  However, Ψre,N shall be calculated with hef only.

hef,mod=maxc'maxc'cr,Nhef,s'maxs'cr,Nhef

s'cr,N,mod=hef,modhefs'cr,N

c'cr,N,mod=hef,modhefc'cr,N

where c'max is the maximum distance from the center of the anchor to the edge of concrete member (<c'cr,N), and

s'max is the maximum center to center distance between anchors (<s'cr,N)

| (42A) CASE WHERE c’1,1 , c’2,1 & c’2,2 ≤ c’cr,N | (42B) Case Where c’1,1 ,c’2,1 , c’2,1 & c’2,2 ≤ c’cr,N |
| --- | --- |

FIG. 42 EXAMPLES OF SPECIAL CASES

9.2.2.3 Pull-out strength of mechanical anchors

The characteristic pull-out strength shall be taken from the AR of the anchor, depending on the concrete strength and the state of concrete (cracked or uncracked) assumed for design. The pullout strength shall be checked for anchor that is most stressed due to load.

9.2.2.4 Pull-out (bond) strength of adhesive anchors

The characteristic pull-out strength of an individual anchor or an anchor group, shall be determined according to the following equation:

NRk,p=NRk,p0Ap,NAp,N0Ψs,NpΨre,NpΨec,NpΨg,Np

where,

NRk,p0= The characteristic pull-out strength of an adhesive anchor placed in cracked or uncracked concrete and not influenced by adjacent anchors or edges of the concrete member .

NRk,p0=ΨsusπdahefτRk,cr' (for applications in cracked concrete)

NRk,p0=ΨsusπdahefτRk,uncr' (for applications in uncracked concrete)

The values of τRk,cr' & τRk,uncr' are to be taken from AR.

Ψsus=1 for αsus ≤ Ψsus0

Ψsus= Ψsus0+1- αsus  for αsus >Ψsus0

where  Ψsus0 is the product depending factor accounting for the effect of sustained loading on the bond strength of adhesive anchor.  It shall be taken from the AR of the adhesive anchor, and it shall be taken as 0.6 if no value is given.

αsus is the ratio between the value of sustained action (permanent action + permanent component of variable action) and the value of total action considered at limit state.

s'cr,Np= Characteristic spacing for pull-out. In the following equation, τRk,uncr' shall correspond to M25 grade concrete,

=7.3daΨsusτRk,uncr'0.5≤3hef

c'cr,Np= Characteristic edge distance for pull-out

=0.5s'cr,Np

Ψs,Np= Factor to account for discontinuities in the symmetrical stress distribution in the concrete due to edges of the concrete member.

=0.7+0.3c'c'cr,Np≤1.0

Ψre,Np= Factor to account for the negative effect of orthogonal reinforcement (that is, with orientation perpendicular to the direction of the force) in the area of the concrete cone.

=0.5+hef200≤1.0

NOTE ─ If in the area of the anchorage there is reinforcement with a spacing > 150 mm (any diameter) or with a diameter < 10 mm and a spacing > 100 mm then the factor  Ψre,Np shall be taken as 1.0.

Ψec,Np= Factor to account for group effect when different tension loads are acting on the individual anchors of an anchor group.

=11+2eNs'cr,Np≤1 Where there is an eccentricity in two directions, Ψec,,Np shall be determined separately for each direction and the product of both factors shall be inserted in formulaΨg,Np= Factor to account for the effect of failure surface for the anchor group. For individual anchor, this factor shall be taken as 1.0. The characteristic bond value 	τRk shall correspond to the strength and the state of concrete assumed for design (cracked or uncracked).

=Ψg,Np0-s's'cr,Np0..5Ψg,Np0-1≥1.0

Ψg,Np0=n-n-1daτRkφheffck1.5≥1.0

n= No. of anchors in a group

φ = 2.20 for cracked concrete

= 3.14 for uncracked concrete

The constants 2.2 and 3.14 are corresponding to fck

Ac,Np0= Idealized projected concrete cone area of an individual anchor with no influence of edge and spacing on the pull-out strength of the anchor. It shall be calculated by idealizing the concrete cone as a pyramid with a height equal to hef and a base length equal to s'cr,Np (see Fig. 40).

Ac,Np0=s'cr,Np∙s'cr,Np

Ac,Np=  Actual projected concrete cone area of the anchorage at the concrete surface. It is limited by overlapping concrete cones of adjoining anchors as well as by edges of the concrete member when edge and spacing are less than the characteristic values.  Ac,Np  shall be calculated in a manner similar to Ac,N  as shown in Fig. 40 but using the characteristic edge distance (c'cr,Np) and spacing (s'cr,Np) values that correspond to pull-out.

9.2.2.5 Special Case

For anchorages with three or more edges with the largest edge distance less than the critical edge distance for pullout in tension, the calculation of strength as above may lead to very conservative values.  For such cases, the embedment depth,hef, spacing, s'cr,N and edge distance, c'cr,N shall be substituted with their modified values as indicated below for determining the characteristic pull out strength NRk,p  according to

However, Ψre,N shall be calculated with hef only.

hef,mod=maxc'maxc'cr,Nphef,s'maxscr,Nphef

s'cr,Np,mod=hef,modhefs'cr,Np

c'cr,Np,mod=hef,modhefc'cr,Np

9.2.2.6 Determination of splitting strength

The characteristic splitting strength of an individual anchor or an anchor group, shall be determined using the following equation:

NRk,sp=NRk,sp0Ac,NAc,N0Ψs,NΨre,NΨec,NΨh,sp

where,

NRk,sp0 shall be taken as minimum of NRk,c and NRk,p. The factors NRk,c, Ac,N, Ac,N0, Ψs,N, Ψec,N, Ψre,N shall be determined according to 9.2.2.2 but using the characteristic edge distance (c'cr,sp) and spacing (s'cr,sp) values that correspond to splitting, taken from the AR of the anchor.

Ψh,sp= Factor to account for the influence of the actual base material depth (D) on the    splitting strength.  In the following equation, Dmin corresponding to splitting failure shall be used.

Ψh,sp=DDmin23≤max[1,hef+1.5 c' Dmin23 ]≤2

NOTE – This check may be omitted if either of the following conditions are fulfilled:

a) The edge distance in all directions is greater than or equal to 1.2c'cr,sp and the base material is greater than or equal to 2hef.

b) For anchors suitable for use in cracked concrete:

1) Reinforcement is present to limit crack width to 0.3 mm, taking into account the splitting forces according to section 9.3

2) The characteristic strength for concrete cone failure and pull-out failure is calculated for cracked concrete

c) If the edge distance of an anchor is smaller than the value ccr,sp then the presence of longitudinal reinforcement between anchor and edge should be ensured.

9.2.2.7 Special case

The special case for anchorages with three or more edges as defined under 9.2.2.2 shall also apply to splitting failure due to loading.  The modified value of embedment, spacing and edge distance as recommended under 9.2.2.2 shall be calculated using characteristic edge and spacing values corresponding to splitting failure.  However, the range for Ψh,sp for adhesive anchors shall be calculated using the actual value embedment, hef.

9.2.3 Design Strength in Shear

The design strength in shear shall be calculated and checked according to limit state of design for all applicable failure modes as per Table 2.  The minimum strength shall govern.

Table 2 Design Strength Checks in Shear

(Clause 7.2.3)

| Sl No (1) | Strength to Resist Expected Failure Types (2) | Checks for Single Anchor (3) | Checks for Anchor Group (4) |
| --- | --- | --- | --- |
| i) | Steel strength (for shear load without lever arm) | VLd≤ VRk,sγMs | VLd,σ*≤ VRk,sγMs |
| ii) | Steel strength (for shear load with lever arm) | VLd≤ VRk,sγMs | VLd,σ*≤ VRk,sγMs |
| iii) | Concrete pry-out strength | VLd≤ VRk,cpγMc | VLd,g≤ VRk,cpγMc |
| iv) | Concrete edge strength | VLd≤ VRk,cγMc | VLd,g≤ VRk,cγMc |

9.2.3.1 steel strength for shear load without lever arm

The characteristic steel strength, VRk,s0 of an anchor subjected to shear load without lever arm shall be taken from the AR of the anchor.

The characteristic resistance of a anchor (VRk,s) accounting for ductility of the anchor in a group is given by

VRk,s= k1 VRk,s0

k1 is product dependent factor and shall be taken from the AR.

NOTE – If the value of characteristic steel strength is not available in the AR then it may be calculated using the following equation for anchors having uniform cross section along its length.

VRk,s0=0.5Asfu 	[This is applicable only for fu≤1 000 N/mm2]

9.2.3.2 steel strength for shear load with lever arm

The characteristic steel strength, VRk,s of an anchor subjected to shear load with lever arm shall be calculated using the following equation. The characteristic bending strength MRk,s0 , characteristic steel strength NRk,s and the material safety factor γMs shall be taken from AR of the anchor.

VRk,s=αMMRk,sl

where,

aM = Factor to account for degree of fixity of the anchor at the side of the base plate (see 	8.2.2.3)

l= Lever arm (see 8.2.2.2)

MRk,s=MRk,s0[1-NLd(NRk,sγMs)]

NOTE – If the value of characteristic bending strength is not available in the AR then it may be calculated using the following equation for anchors having uniform cross section along its length.

MRk,s0=1.2Zelfu

9.2.3.3 Determination of concrete pry-out strength

The characteristic concrete pry-out strength (see Fig. 43) of an individual anchor or an anchor group, shall be determined according to the following equations.

For mechanical anchors, VRk,cp=kcpNRk,c

For adhesive anchors: VRk,cp=minkcpNRk,p,kcpNRk,c

The factor kcp shall be taken from the relevant assessment report.

NOTE – In cases where the anchor group is loaded by shear loads and/or external torsion moments, the direction of the individual shear loads may change. Fig 44 demonstrates this for a group of two anchors loaded by a torsion moment. The above equations are not suitable for this application.  The shear loads acting on the individual anchors neutralize each other and the shear load acting on the entire group (VLd) is 0.

FIG. 43 TYPICAL CONCRETE PRY-OUT FAILURE

FIG.44 GROUP OF ANCHORS LOADED BY TORSION MOMENT

When the horizontal or vertical components of the shear loads on the anchors change direction within a group (for example, torsion or inclined shear), the verification of pry-out failure for the entire group shall be substituted by the verification of pry-out failure for the most unfavorably positioned and loaded anchor of the group.  When calculating the strength of the most unfavorable anchor, the influences of both edge distances as well as anchor spacing shall be considered.  This shall be done by using the  Ac,N for the most unfavorably loaded anchor in NRk calculation for determining concrete pryout strength using above equation.  Examples for the calculation of Ac,N for individual anchors of an anchor group are illustrated in Fig. 45.

(45A) GROUP OF FOUR ANCHORS WITHOUT EDGE INFLUENCE

(45B) GROUP OF TWO ANCHORS IN A CORNER

FIG. 45 EXAMPLES OF ACTUAL PROJECTED CONCRETE CONE AREA (AC,N)

FOR INDIVIDUAL ANCHORS IN A GROUP

9.2.3.4 Concrete edge strength

The characteristic concrete edge strength of an individual anchor or an anchor group, shall be determined according to the following equation.  For anchorages placed at a corner, the strengths for both edges shall be calculated, and the smallest value shall govern.

VRk,c=VRk,c0Ac,VAc,V0Ψs,VΨre,VΨec,VΨh,VΨα,V

In case of an anchor group with filled clearance holes and more than one row in direction of the shear load each crack plane shall be considered separately. The verification shall be made for each crack plane.

This has been elaborated in Fig 48.

The resolution of shear force within an anchor group and the corresponding verification for the crack plane has been illustrated in Annex A

In case the hole filling cannot be conformed at site, only the capacity of the front row anchors shall be considered for concrete edge break-out verification.

VRk,c0= The characteristic strength of a single anchor placed in cracked or uncracked concrete, loaded perpendicular to the edge in shear and not influenced by adjacent anchors or edges of the concrete member

=1.55dαhefβfckc'11.5 (for applications in cracked concrete)

=2.18daαhefβfckc'11.5  (for applications in uncracked concrete)

The constants 1.55 and 2.18 are corresponding to fck

α=0.1hefc'10.5

β=0.1dac'10.2

s'cr,V=3c'1=2c'cr,V

Ψs,V=Factor to account for discontinuities in the symmetrical stress distribution in the 	concrete due to edges of the concrete member on shear strength.

For anchorages with the edges parallel to the direction of load (for example in a narrow concrete member), the smallest edge distance shall be used as c'2 in the 	following equation.

Ψs,V=0.7+0.3c'21.5c'1≤1.0

Ψre,V= Factor to account for effect of reinforcement in cracked concrete.

=1.0 (For anchorage in uncracked concrete and anchorage in cracked

concrete without edge reinforcement)

=1.4 (For anchorage in cracked concrete with edge reinforcement and

closely spaced stirrups (spaced at less than or equal to 100 mm)

Ψec,V= Factor to account for group effect when different shear loads are acting

on the individual anchors of an anchor group.

=11+2eVs'cr,V≤1

Ψh,V= Factor to account for member thickness

=1.5c'1D0.5≥1

Ψα,V= Factor to account for the angle αV between the load applied, VLd, and

the direction perpendicular to the free edge of the concrete member

(αv ≤ 90°).

=1cosαV2+0.5 sinαV2≥1.0

NOTE – In case αV > 90° it shall be assumed that only the component of the shear load parallel to the edge is acting on the anchor.  The component acting away from the edge may be neglected for checking concrete edge failure.

Ac,V0= Idealized projected concrete cone area of an individual anchor at the lateral 	concrete surface with no influence of edge, spacing and member thickness on the concrete edge strength of the anchor.  It shall be calculated by idealizing the concrete edge cone as half pyramid with height equal to 1.5c1  and a base length equal to 3c'1 (see Fig. 46).

Ac,N0=4.5c'12

Ac,V=  Actual projected concrete cone area of the anchorage at the lateral concrete surface.  It is limited by overlapping concrete cones of adjoining anchors, member thickness as well as by edges of the concrete member parallel to the assumed load direction (see Fig. 47).

NOTE – For the calculation of Ac,N0 and Ac,V it is assumed that the shear loads are applied perpendicular to the edge of the concrete member.

FIG. 46 IDEALIZED PROJECTED CONCRETE CONE AREA, AC,V0 OF AN INDIVIDUAL ANCHOR

(47A) SINGLE ANCHOR AT A CORNER

(47B) GROUP OF ANCHORS AT AN EDGE IN A THIN CONCRETE MEMBER

(47C) GROUP OF ANCHORS AT CORNER IN A THIN CONCRETE MEMBER with unfilled clearance holes (front anchor take the shear load perpendicular to the edge)

FIG. 47 EXAMPLES OF ACTUAL PROJECTED CONCRETE CONE AREA FOR DIFFERENT ANCHOR CONFIGURATIONS SUBJECTED TO SHEAR LOAD

FIG. 48 CRACK PLANES WITH A GROUP OF 8 ANCHORS WITH A SHEAR LOAD PERPENDICULAR TO THE EDGE WITHIN THE RESPECTIVE CRACK PLANE FOR FILLED HOLES

|  |  | Loads directed away from the edge, hence no proof for concrete edge failure needed. |
| --- | --- | --- |
| (49A) GROUP OF ANCHORS AT AN EDGE LOADED BY Vld With An Angle αv = 180° |  |  |
| Total Load Action |  |  |
| Load on each anchor |  | Load components directed away from the edge are neglected |
| Load on anchor group for calculations |  |  |
| (49B) GROUP OF ANCHORS AT AN EDGE LOADED BY vld With An Angle 90 °< αv < 180° |  |  |
| Total load Action |  |  |
| Load on each anchor |  | Load components directed away from the edge are neglected |
| Load on anchor group for calculations |  |  |
| (49C) GROUP OF ANCHORS AT THE EDGE LOADED BY A TORSION MOMENT |  |  |

FIG. 49 EXAMPLES OF ANCHOR GROUP AT EDGE LOADED BY SHEAR FORCE OR TORSION

| Action |  |  |  |
| --- | --- | --- | --- |
| Load on each anchor |  |  |  |
| Load on anchor group |  |  |  |
| Load on anchor group for calculations |  |  |  |
| Action |  |  |  |
| Load on each anchor |  |  |  |
| Load on anchor group |  |  |  |
| Load on anchor group for calculations |  |  |  |

FIG. 50 EXAMPLES OF ANCHOR GROUP AT EDGE LOADED BY SHEAR FORCE AND TORSION

9.2.3.4.1 Special Case

For anchorages in a narrow or thin member (D<1.5c'1) with the largest edge distance less than the characteristic edge distance of 1.5c'1 in shear, the calculation of strength according to 9.2.3.4 may lead to very conservative values. For such cases, the edge distance c1 shall be substituted with modified value c'1 as indicated below in all equations in 9.2.3.4.

For single anchor

c'1=maxc'2max1.5,D1.5

For group of anchors,

c'1=maxc'2max1.5,D1.5,s'2max3

Where s'2max is the maximum spacing between the anchors in the orthogonal directions

FIG. 51 EXAMPLES OF ANCHORAGE IN A THIN NARROW MEMBER

9.2.4 Check for Combined Tension and Shear

The following equations shall be satisfied for combined tension and shear loads (seeFig. 52).

βN  <  1

βV  <  1

(βN) + (βV)  < 1.2	(for failure mode other than steel)

Or

(βN)a + (βV)a  < 1

where,

a  = 2.0, if NLd and VRd are governed by steel failure, and

a  = 1.5, for all other failure modes

bN and bV =   Ratio between design load and design strength for tension and shear loading, respectively.  The largest value of bN and bV for the different failure modes shall be taken.

FIG. 52 INTERACTION DIAGRAM FOR COMBINED TENSION AND SHEAR LOADS

10 DESIGN OF POST-INSTALLED ANCHORING SYSTEMS FOR EARTHQUAKE EFFECTS

10.1 General

The basic design requirement and provisions for static conditions shall also apply to design of anchor for seismic conditions.  The partial safety factors recommended for static conditions are applicable for seismic design as well.  In addition, the requirements of this section shall be fulfilled.

10.1.1 Anchors

As a prerequisite for seismic design, the anchors shall be tested and evaluated as per seismic test provisions in addition to cracked assessment requirements.  Appropriate measures shall be adopted to avoid loosening of nut during seismic event (for example, double nut).  Further, it shall be assumed that anchors do not dissipate energy by means of ductile hysteretic behavior and do not contribute to the overall ductile behavior of the structure.  Stand-off fastening or other configurations where anchors may be subjected to shear load with lever arm shall not be permitted under seismic conditions.  Base plates with grout layer shall not be permitted under seismic conditions.

10.1.2 Location of Anchors

The gap between the base plate clearance hole and the anchor should be avoided in seismic conditions.  If it is not possible to avoid this gap, then the factor αgap shall be applied to account for the effect of this gap on behavior of the anchor.  However, the clearance diameter df shall be limited to the values given in 7.3.1.

10.1.3 Applicability of Seismic Design Provisions

For all seismicity levels defined as per IS 1893, anchor shall be designed for seismic conditions.  The design seismic force acting on the base plate shall be determined according to IS 1893 (Part 1) and other relevant standards.

NOTE

1 When the seismic tension component of the design force at the ultimate limit state applied to an individual anchor or an anchor group is equal to or less than 20 per cent of the total design tensile force, then seismic provisions in 10.2 need not apply for the verification of the tension component acting on a single anchor or a group of anchors.

2 When the seismic shear component of the design force at the ultimate limit state applied to an individual anchor or an anchor group is equal to or less than 20 per cent of the total design shear force, provisions in 10.2 need not apply for the verification of the shear component acting on a single anchor or a group of anchors.

3 The seismic forces may be considered for non-structural components also. Specialist literature may be consulted for understanding on how to derive seismic forces on anchor and how to account for amplification of seismic forces. Reference to IS 1893 or IS 16700 may be made in this regard for calculation of seismic force on non-structural elements.

10.2 Design Options

The anchor shall be designed for seismic condition as per 10.2.1 or 10.2.2 or 10.2.3.

10.2.1 Capacity Design

As per this method, an individual anchor or an anchor group shall be designed for the maximum tension and/or shear load that can be transmitted to the anchor based on either the development of a ductile yield mechanism in the attached element (see Fig. 53A) or the base plate (see Fig. 53B) taking into account strain hardening and the capacity of a non-yielding attached element (or structural element) (see Fig. 53C).

NOTE – The assumption of a plastic hinge in the base plate (see Fig. 53B) requires to take into account aspects like the redistribution of loads to the individual anchors of a group, the redistribution of the loads in the structure, the fatigue behavior of the base plate, etc.

| 53A YIELDING IN ATTACHED ELEMENT | 53B YIELDING IN BASE PLATE | 53C CAPACITY OF ATTACHED ELEMENT |
| --- | --- | --- |

FIG. 53 SEISMIC DESIGN BY PROTECTION OF ANCHOR (see 10.2.1)

10.2.2 Elastic Design

As per this method, an individual anchor or an anchor group shall be designed for the maximum load obtained from the design load combinations (including seismic) corresponding to the limit state (refer IS 1893 Part 1) assuming an elastic behavior of the anchorage and of the structure.  Furthermore, uncertainties in the model to derive seismic forces on the anchorage shall be taken into account.

10.2.3 Design with Requirements on the Ductility of the Anchors

This method shall not be used for anchor connections of primary seismic members. This method may be used only for secondary/tertiary seismic member. As per this method, an individual anchor or an anchor group shall be designed for the maximum load obtained from the design load combinations (including seismic) corresponding to the limit state (refer IS 1893).  The tension steel capacity of the anchor or anchor group shall be smaller than the tension capacity in concrete related failure modes.  Elongation capacity of the anchors shall be such that it accommodates the deformation according to the seismic analysis of the connection.

10.2.3.1 For this design method, the following requirements shall apply:

- The anchor shall have technical assessment report (AR) that includes qualification for seismic performance.

- To ensure steel failure mechanism, following shall be satisfied:

For single anchor in tension: NRk,s,seis≤0.7NRk,c,seisγinst

For anchor group in tension: NRk,s,seisNLd,σ*≤0.7NRk,c,seis(NLd,g∙γinst)

In addition to the above requirement, the following shall apply to the highest loaded anchor for group of mechanical anchor in tension:

NRk,s,seis≤0.7NRk,p,seisγinst

where,

NRk,s,seis = Characteristic seismic steel strength

NRk,c,seis = Characteristic seismic strength for all non-steel failure

types like concrete cone, blowout

and splitting failure.

NRk,p,seis = Characteristic seismic pullout strength

γinst  = Partial safety factor for installation safety.

NLd,σ*  = Design load on the most stressed anchor of an anchor

group and

NLd,g = Design load on the tensioned anchors of an anchor

group.

- Anchors for tension load shall be ductile and shall have a stretch length of at    least 8da (see Fig. 54) or more as per the analysis requirement.

FIG. 54 SEISMIC DESIGN BY YIELDING OF A DUCTILE ANCHOR – ILLUSTRATION OF STRETCH LENGTH

- An anchor shall be considered as ductile if the nominal steel yield strength ((fy) of the load transferring section does not exceed 650  MPa, the ratio of nominal yield strength (fy) to nominal ultimate strength (fu) does not exceed 0.8, and the rupture elongation (measured over a length of 5da) is at least 12 percent.

- The characteristic steel strength (resistance) of the anchors that incorporate a reduced section over a length smaller than 8da,red (da,red = anchor diameter of reduced section) shall be greater than 1.3 times the characteristic yield capacity (resistance) of the unreduced section as per AR.

10.3 Design Method

The design strength shall be calculated according to limit state of design for all load directions namely, tension, shear individually or combined as well as for all applicable failure modes.  The minimum strength shall govern for each load direction.

10.3.1 Partial Safety Factors

Partial safety factor of material for static design (see 9.2.1) shall also be applicable for seismic design.

10.3.2 Design Check in Tension and Shear

The design strength in tension and shear shall be calculated and checked according to limit state of design for all applicable failure modes as per Table 3.  The minimum strength shall govern for each load direction.

Table 3 Design Strength Checks in Tension and Shear for Seismic Design

(Clause 10.3.2)

| Sl No. | Parameter | Checks for Anchor |
| --- | --- | --- |
| (1) | (2) | (3) |
|  | Strength to resists expected failure types in tension |  |
|  | Steel strength | NLd,seis≤ NRk,s,seisγMs |
|  | Concrete cone strength | NLd,seis≤ NRk,c,seisγMc |
|  | Pull-out strength (MA) (see Note 1) | NLd,seis≤ NRk,p,seisγMp |
|  | Pull-out strength (AA) (see Note 1) | NLd,seis≤ NRk,p,seisγMp |
|  | Splitting strength (see Note 3) | NLd,seis≤ NRk,sp,seisγMsp |
| ii) | Strength to resists expected failure types in shear |  |
|  | Steel strength (For shear load without lever arm) (see Note 2) | VLd,seis≤ VRk,s,seisγMs |
|  | Concrete pry-out strength | VLd,seis≤ VRk,cp,seisγMc |
|  | Concrete edge strength | VLd,seis≤ VRk,c,seisγMc |

NOTES

1 MA – Mechanical anchor and AA – Adhesive anchor.

2 Steel failure for shear load with lever arm is not covered in this standard.

3 Check for splitting failure shall not be required if cracked concrete is assumed and

reinforcement is available in base material (that is concrete) to resist splitting forces.

10.3.2.1 Determination of characteristic strength

The characteristic strength for an anchor or an anchor group shall be determined for each failure type as follows:

RRk,seis=αgapαseisRRk, seis0

where

αgap = Reduction factor to account for inertia effects due to any gap between 		 anchor and base plate in shear; as given in the relevant AR.

NOTE – If αgap value is not available in AR then αgap may be assumed to be 1.0 in case of no hole clearance between anchor and base plate and 0.5 in case of connections with hole clearance (dfix) as given in 7.3.1.

αseis= Reduction factor to account for the influence of large cracks and scatter

of load-displacement curves (see Table 4)

RRk, seis0 = Characteristic seismic resistance of a single anchor for a given failure mode and not influenced by adjacent anchors or edges of the concrete member determined as per Table 5.

Table 4 Reduction Factor for Seismic Design αseis

(Clause 10.3.2.1)

| Sl No. | Parameter | For Single Anchor | For Anchor Group |
| --- | --- | --- | --- |
| (1) | (2) | (3) | (4) |
| 1) | Failure type in tension |  |  |
| a) | Steel failure | 1 | 1 |
| b) | Concrete cone failure |  |  |
|  | i) Undercut anchor | 1 | 0.85 |
|  | ii) All other anchors | 0.85 | 0.75 |
| c) | Pull-out failure for mechanical anchor | 1 | 0.85 |
| d) | Pull-out failure adhesive anchor | 1 | 0.85 |
| e) | Splitting failure | 1 | 0.85 |
| 2) | Failure type in shear |  |  |
| a) | Steel failure (For shear load without lever arm | 1 | 0.85 |
| b) | Concrete pry-out failure |  |  |
|  | i)Undercut anchor | 1 | 0.85 |
|  | ii) All other anchors | 0.85 | 0.75 |
| c) | Concrete edge failure | 1 | 0.85 |

Table 5 Determination of RRk, seis0

(Clause 10.3.2.1)

| Sl No. | Parameter | Method of Determination of Characteristic Seismic Resistance RRk, seis0 |
| --- | --- | --- |
| (1) | (2) | (3) |
| i) | Strength to resists expected failure types in tension |  |
|  | Steel strength | As per AR of the anchor |
|  | Concrete cone strength | Same as that for static condition (See 9.2) |
|  | Pull-out strength for mechanical anchor | As per AR of the anchor |
|  | Pull-out strength for Adhesive Anchor | As per 9.2.2.4 using the characteristic bond resistance for seismic τRk,seis as per AR shall be used |
|  | Splitting strength | Same as that for static condition (see 9.2) |
| ii) | Strength to resists expected failure types in shear |  |
|  | Steel strength (For shear load without lever arm) | As per AR of the anchor |
|  | Concrete pry-out strength | Same as that for static condition (see 9.2) |
|  | Concrete edge strength | Only first row of anchor to be considered. (see 9.2) |

Note – The design of fastenings under earthquake loading for earthquake zones III and above and for important building classes (as per NBC 2016 and IS 1893) shall be based on an assessment under pulsating tension, crack cycling under constant tension load and alternating shear in cracked concrete at a crack width of 0.8 mm.

10.3.3 Check for Combined Tension and Shear

The following equations shall be satisfied for combined tension and shear loads:

NLd,seisNRd,seis≤1

VLd, seisVRd,seis≤1

NLd,seisNRd,seis+VLd, seisVRd,seis≤1

where the largest ratio for NLd,seisNRd,seis and VLd,seisVRd,seis for different failure types shall be inserted in the above equations. The interaction checks shall be separately performed for steel and concrete failures.

10.3.4 Displacements

The anchor displacement under tensile and shear load at limit state of displacement shall be limited to  δN,reqDLS and δV,reqDLS value of the application to meet requirements regarding functionality and assumed support conditions.  If anchor and attached elements are expected to be operational after an earthquake then relevant anchor displacements shall be taken into account.  If the anchor displacements δN,seisDLS under tension loading and/or δV,seisDLS under shear load provided in the relevant AR are higher than the corresponding required values δN,reqDLS and/or δV,reqDLS, the design resistance may be reduced according to the following equations:

NRd,seis,red=NRd,seisδN,reqDLS δN,seisDLS

VRd,seis,red=VRd,seisδV,reqDLS δV,seisDLS

NOTE – When a rigid support is assumed in the analysis the designer shall establish the limiting displacement compatible to the requirement for the structural behavior. The acceptable displacement associated to a rigid support condition is considered to be 3 mm.

If the connection such as façade element is designed to accommodate deformations (that is displacements or rotations) then it shall be demonstrated that the anchor can accommodate these deformations.  The rotation of a connection θ (see Fig. 55) is given by

θ=δN,seiss'max

where,

δN,seis 	= Displacement of the anchor (limited to 3 mm) when subjected to earthquake load

s'max 	= Distance between the outermost row of anchors and the opposite edge of the 		    base plate

FIG. 55 EXAMPLE OF ROTATION AND DISPLACEMENT OF A CONNECTION

11 ADDITIONAL CHECKS AND REQUIREMENTS

11.1 General

To establish the transmission of the anchor loads to the supports of the concrete member, basic checks shall be carried out with due consideration of the loads introduced by the anchors along with additional provisions given in this section.

NOTE – In the case of slabs and beams made out of prefabricated units and added cast-in-situ concrete, anchor loads may be transmitted into the prefabricated concrete only if the precast concrete is connected with the cast-in-situ concrete by shear reinforcement. If this shear reinforcement between precast and cast-in-situ concrete is not present, the anchors shall be designed as per the provisions of this standard.

11.2 Shear Strength of Concrete Member

The shear forces VLda caused by anchor loads shall not exceed the value 0.4VRd1; where VRd1 is design shear strength of concrete according to IS 456.  When calculating VLda the anchor loads shall be assumed as point loads with a width of load application t1=s't1+2hef and t2=s't2+2hef, where s't1 and s't2 is spacing between the outer anchors of a group in direction 1 and 2, respectively.

11.3 Resistance of Concrete Member to Splitting

The splitting forces generated by anchors shall be taken into account while designing the concrete member.  This requirement may be neglected if one of the following conditions is met:

- The load transfer area that is the embedment length along which load is transferred) of anchor is in the compression zone of the concrete member.

- The tension component of the characteristic loads acting on the single anchor or anchor group is less than 10 kN.

If tension component of the characteristic loads is greater than 10 kN but less than 30 kN, the splitting check may still be neglected

- if the area of the transverse reinforcement is at least 60 percent of the longitudinal reinforcement required for the loads due to anchor loads.

- For fastenings in slabs and walls wherever reinforcement in both directions is present as per IS 456 in the region of the anchorage.

If the tension component of the characteristic loads acting on the anchorage is greater than or equal to 30 kN and the anchors are located in the tension zone of the concrete member then the splitting forces shall be taken up by reinforcement.  The ratio between splitting force FRk,sp and the tension component of the characteristic loads NL,Rk shall be taken as:

FRk,sp = 0.5 NL,Rk , for adhesive anchors

FRk,sp = 1.5 NL,Rk, for torque controlled expansion anchors

FRk,sp= 1.0 NL,Rk , for undercut (mechanical) anchors

FRk,sp= 2.0 NL,Rk , for deformation controlled expansion anchors

ANNEX A

ILLUSTRATION OF SHEAR LOAD VERIFICATION FOR DIFFERENT LOAD COMBINATIONS WHEN HOLES ARE FILLED UP

Case 1 – Only shear force acting towards the edge

|  | Loads to be considered | Resistance to be considered |
| --- | --- | --- |
| Crack Plane 1 | VV= V2 | Resistance considering c'= c1' |
| Crack Plane 2 | VV= V | Resistance considering c'= c2' |

Case 2 – Shear force verification due to torsion

|  | Loads to be considered | Resistance to be considered |
| --- | --- | --- |
| Crack Plane 1 | VH= VH1+ VH2 VV= VV1 | Resistance considering c'= c1' |
| Crack Plane 2 | VH= VH3+ VH4 VV= VV1+ VV3 | Resistance considering c'= c2' |

Case 3 – Shear force verification due to combination of shear force and torsion acting simultaneously

|  | Loads to be considered | Resistance to be considered |
| --- | --- | --- |
| Crack Plane 1 | VH= VH1+ VH2+ VX2 VV= VV1 | Resistance considering c'= c1' |
| Crack Plane 2 | VH= VH3+ VH4+ VX2 VV= VV1+ VV3 | Resistance considering c'= c2' |

- Shear load parallel to edge

|  | Loads to be considered | Resistance to be considered |
| --- | --- | --- |
| Crack Plane 1 | VH= VH1+ VH2 VV= VV1+ VY2 | Resistance considering c'= c1' |
| Crack Plane 2 | VH= VH3+ VH4 VV= VV1+VV3+ VY | Resistance considering c'= c2' |

- Shear load towards the edge

NOTE: All the resolved forces on the anchors are to be considered as concentric with the anchors.

ANNEX B

LIST OF CROSS REFERRED INDIAN STANDARDS

| IS No. | Title |  |
| --- | --- | --- |
| IS 1946 | Fixing Devices In Walls, Ceilings And Floors Of Solid Construction |  |
|  | Part 1 | Devices Other Than Post-Installed Anchors - Code of Practice |
|  | Part 3 | Testing and Assessment Of Post-Installed Adhesive Anchoring Systems |
|  | Part 4 | Testing and Assessment of Post-Installed Mechanical Anchoring Systems |
|  | Part 5 | Post-Installed Anchorage to Concrete -Installation and On-site Inspection – Code of Practice |
| 1608 (Part 1) | Mechanical testing of metals - Tensile testing |  |
| 1893 (Part1):2016 | Criteria for earthquake resistant design of structures (sixth revision) |  |
| 456 :2000 | Plain and reinforced concrete - Code of practice (fourth revision) |  |
| 875 (Part 1) : 1987 | Code of practice for design loads (Other Than Earthquake) for buildings and structures: Part 1 dead loads - Unit weights of building materials and stored materials (second revision) |  |
| 875 (Part 2) : 1987 | Code of practice for design loads (Other Than Earthquake) for buildings and structures: Part 2 imposed loads. (second revision) |  |
| 875 (Part 3) : 2015 | Design Loads (Other than Earthquake) for Buildings and Structures - Code of Practice Part 3 Wind Loads (third revision) |  |
| 875 (Part 4) : 2021 | Code of practice for design loads other than earthquake for Buildings and Structures Part 4 Snow Loads |  |
| 875 (Part 5) : 1987 | Code of practice for design loads (Other Than Earthquake) for buildings and structures: Part 5 special loads and load combinations (second revision) |  |
| 16700 : 2017 | Criteria for structural safety of tall concrete buildings |  |

ANNEX C

(Foreword)

INSTALLATION AND INSPECTION

Installation of anchors shall be in accordance with the manufacturer printed installed instruction (MPII) and safety data sheet for the respective anchor. The anchor installation should be undertaken by installers who have been adequately trained by a competent trainer or manufacturer. The installer should be familiar with the correct installation procedures and ensure that the correct drilling and setting tools are available for the proper installation of the anchor.

Following installation and prior to loading, the anchors should be inspected so that any observations regarding rotation, movement, deformation, cracking, or other damage can be recorded and communicated to the concerned engineer-in-charge for corrective measures.

Testing of anchors on site may be required after installation to validate the quality of installation. These proof tests should be carried out on a sample of working anchors on safety-critical application (unless approved anchors have been installed by trained operators working under supervision), after the anchors have been installed, to ensure that they have been installed correctly. The tests are intended to demonstrate that anchors to be used in service have a modest safety margin without risking their integrity.

This is covered in IS 1946 Part 5.

Users of anchors are encouraged to verify the testing/assessment reports issued by reputed bodies who would demonstrate independently the above mentioned criteria.

ANNEX D

REFERENCE TO ASSESSMENT REPORTS

The Assessment Report (AR) for post-installed anchor is issued by an Approval Body, which is an institute of national/ international acceptance/ recognition having experience in the field of testing and assessment of post installed anchors based on tests carried out by the Third Party Laboratory.

A suggestive format detailing out the procedure for issuance of assessment report is provided in IS 1946 Part 3 and IS 1946 Part 4

An example of globally accepted AR is a European Technical Assessment (ETA) which is issued by an Approval Body (known as Technical Assessment Body in Europe). This is done as per the testing and assessment of post-installed anchors based on the test protocols of EOTA EAD 330499 “European Assessment Document – Bonded Fasteners for Use in Concrete” and EOTA EAD 330232 “European Assessment Document – Mechanical Fasteners for Use in Concrete”.

The anchors, tested and assessed as per global test protocols which are more stringent or at least meet the requirement of the given standard, may be used.

Some of the globally established Approval Bodies capable of issuing AR for post-installed anchors are

- CSTB - Scientific and Technical Center for Building, France

- DIBt – Deutsches Institut für Bautechnik – Centre of Competence in Construction Engineering, Germany

- ITAB/ITC-CNR – Italian Technical Assessment Body/Construction Technologies Institute, Italy

- STC - Public Central Technical Service for Construction, Italy

- ERO - Element Materials Technology Rotterdam B.V., Netherlands

- KIWA - Certification and Inspection, Netherlands

- IBDIM - Road and Bridge Research Institute - Instytut Badawczy Drog i Mostow, Poland

- ITB - Building Research Institute - Instytut Techniki Budowlanej, Poland

- EMPA – Swiss Federal Laboratory for Materials Science & Technology, Switzerland

- OIB - Austrian Institute of Construction Engineering, Austria

- ETA-DANMARK A/S, Denmark

In contrast to the design considerations in India, the anchor design as per European standards is based on cylindrical concrete strength.

In case, the designer wants to refer to the value of kcr,N / kucr,N taken directly from the ETA for checking adequacy against concrete cone failure, he/she would be required to make the following modifications in the calculation (see 9.2.2.2) -

NRk,c0=kcr,Nfckhef1.51.1 for cracked concrete

NRk,c0=kucr,Nfckhef1.51.1 for uncracked concrete

ANNEX E

(Committee composition will be added after finalization)

*******