# Indian	Standard

APPLICATION GUIDE FOR

ELECTRICAL RELAYS FOR ac SYSTEMS

#### PART II	OYERCURREHT RELAYS FOR

GENERATORS AND MOTORS

( Si.xth Reprint AUGUST 1996 )

UDC 621.316.925.43:621.3 13

O  C'op›u‘i¿lit  1967

D II II E A U	O F	I  N D I A N	S T A N D A R D S MANAK BI IA VAN, 9  B.AI IAD UR SI IAH ZAFAR MAR G N EW D E LI1 I 11(1002

Marcb 1967

# Indian	Standard

APPLICATION GUIDE FOR ELECTRICAL RELAYS FOR ac SYSTEMS

PART II	OVERCURRENT RELAYS FOR GENERATORS AND btOTORS

#### Relays Sectional Committee, ETDC 3â

Tata Hydro-Electric Power Supply Go Lid, Bombay

Shri K. M. Chinnappa )

Sagi  M. C. Bxsavxzinoxixo	Mysore State Electricity Board, Bangalore gear S.K. B+txns	Heavy Eltctrical• t India ) Ltd, Bhopal

Star A. RaJzazo Alrrnat‹ 1

Scar V.S. Baxzia	Siemens Engineering and Manufacturing Co of India

Ltd, Bombay

Seaz A. Dana	J	' *imiled, Baroda

Seri B.K. Muxiizmas	National Test House, Calcutta

Syst R. Psnuxnzaoxu	The Tata Iron and Steel Co Ltd, Jamshedpur

Snei S.G. Pxazsoz	Directorate General of Supplies & Disposals ( Inspec-

tion Wing ) ( Ministry of Supply, Technical Development & Materials Planning )

The English Electric Co of India Ltd, Madras

Paor  H.  N. Rxux en xxnez R xo	Indian Institute of Science, Bangalore San     P. Renoxawau v	Hindustan Steel Limited, Ranchi

Seri  V. Ssszs•sxu xiv	Railway Board ( Ministry of Railways ) Suai P.K. See	Punjab State Electricity Board, Patiala

Seat  C.S. S+tsunivzsxx	Central Yt'ater & Power Commission ( Power Wing )

Directorate General of Posts & Telegraphs    rransport & Communications )

Sun     H.S. Viawaawaniza	Radio & Electricals Manufacturing Co Ltd, Bangalore STfni  Y. S.  VEnznzsswanan.	Director Generals BIS ( ñ•-•Qcio Member )

Director ( Elec tech )

Srisi R. C. BxJrni Assistant Director ( Elec tech )

BUR   E AU	O F	I N D IAN	STAND A R D S MANAK BHA VAN, 9  BAHADUR  SHAH  ZAFA R  MARO NEW   DELHI 110002

Pa nel for Application Guide for Electrical Relays, ETDC 35/ P2

PxorH.N.R*x*ca*xoxAR&o

Siisi M. C. Bxsavaziuoaizit Siisi S. K. Benzix

Siiai N. Nama Suzi P. K. Szn

Siisi G. S. Terms

Indian Institute of.Science, Bangalore

lvlysore State Electricity Board, Bangalore Heavy Electricals ( India ) Ltd, Bhopal

The Engl ish Electric Co of Ind ia Ltd, Madra.s Punjab State Electricity Board, Patio la

Tata Hydro-Electric Power Supply Co Ltd, Bombay

# Indian	Standard

APPLICATION GUIDE FOR

ELECTRICAL RELAYS FOR ac SYSTEMS

PART I I	OVERCURRENT RELAYS FOR GENERATORS AN D f*lOTORS

## 0.	F O R E W O R D

  - This Indian Standard ( Part II ) was adopted by the Indian Standards Institution on 19 December l9Gfi, after the draft finalized by the Relays Sectional Committee had been approved by the Electrotechnical Division Council.

  - Modern power systems are designed to provide uninterrupted electrical supply, yet the possibility of failure cannot be ruled out. The  protective relays stand watch and in the event of failures, short-circuits or abnormal operating conditions help de-energize the unhealthy section of the power system and restrain interference with  the  remainder  of  it  and  thus  limit damage to equipment  and  ensure safety of  personnel. They  are  also  used to indicate the type and location of failure so as to assess the effectiveness of the protective schemes.

  - In spite of the many refined protective schemes available today, the overcurrent protection has held its osvn because of its simplicity and econo- mical   cost.   Subsequent   to   the   publication   of   IS : 3231-1965*,   it   was felt  that  an  application guide  for  overcurrent  relays  be   prepared   so  that  the system planning engineers may select and apply the overcurrent relays correctly from among the multitude of those available today.

  - The features which the protective relays should possess are:

    - Relialaility, that is, to  ensure  correct  action  even  after  icia¿c  J  eriods of inactivity and also offer repeated  opei ations  under  severe  condi- tions;

    - Selectivity, that is, to ensure that only the unhealthy part of the system is disconnected;

    - Sensitivity, that is, detection of the short-circuit or abnormal operating condition;

    - Speed to prevent or minimize damage ate d risk of instability of rotating plant; and

°Specification fo r electrical relays for power system protection .

3

### Stability, that ii, the ability to operate only under those conditions that call for its operation and to remain either passive or biaied against operation under all other conditions.

  - Thii  guide  dealt  mirth  only  those   relays   wiiich   are  covered   by   IS : 3231-1965*. When overcurrent protection for motors is provided in the  motor starters reference should be made to IS : 1822 -1967 and IS : 3914-

  - This guide hai been  prepared  mainly  to hssist  protection  engineer in application of overcurrent relays installed as a separate  unit for genera-  tors and motors. Few practical exarpples have also been included to illustrate the application of these relays, their settings, etc. However, it is emphasized that this guide has been prepared to assist rather than to specify the relay to be used. This guide deals only with the principles of application of overcurrent relays and does not deal with the selection of any particular protective scheme. The actual circuit conditions in all probability may be different from those described here. The examples, even though drawn from actual field applications, should be regarded as mere illustration  of one  or the other point.

  - In the preparation of this guide considerable assistance has been derived from several published books and from manufacturers’ trade literature. Assistance has also been rendered by State Electricity Boards in collecting actual examples.

  - This guide is one of the series  of  Indian  Standard  application  guides for electrical  relays  for  ac  systems.  The   other   guides   in   this  series are:

IS : 3638-1966 Application guide for gas-operated relays

IS : 3842 ( Part I ) -1967 Application guide  for  electrical  relays  for ac systems: Part I Overcurrent relays for feeders and transformers

IS : 3842 ( Part III )-1966 Application guide liar electrical  relays  for ac systems: Part I II Phase unbalance relays including negative phase sequence relays

IS : 3842 (  Part  IV )-1966  Application guide  for  electrical  relays  for ac systems: Part IV Thermal relays

•.Specificatfon for electrical relays for power system protection.

}S§ecification for ac motor starters of voltage not exceeding 1 000 t›I ts ( fret rei ision j

t Code of practice for selection of ac induction motor starters ( s oltage not exceeding

1 00b YOl ts ) •

## 4

I.8COPE

I.1 This guide deals with application of overcurrent relays for  ac  systems covered by IS : 3231-1965* for generators and motors.

#### This guide does not cover:

    - the principles of system design and system protection, and

    - application of such relays which form an integral part of a motor starter.

- TERMINOLOGY

  - For  the purpose   of   this  guide,   the   definitions   given   in   IS : 1885 ( Part IX )-1966{ and Part I of this guide shall apply.

### OVERCURRENT RELAYS FOR GENERATORS

8.1 General

#### 3.1.i Overcurrent relays have a limited application in the protection  schemes for generators as they  cannot  provide  as  good  a  protection  for  the generators as differential relays. They are principally applied to provide back-up protection  for  sustained  external  faults,  that  is,  on  the  bus-bars or on the feeders. However, they also act as back-up to the differential protection on internal faults where bus-bars can feed into the faults.

3.1.2 Simple inverse definite minimum time-lag (  IDMTL  )  overcurrent relays as described for the protection of feeders and transformers are, in general, unsatisfactory for phase-to-earth fault back-up protection because certain methods of earthing of the generator, that is, distribution  transformer or voltage transformer earthing limit the maximum available earth fault current to a value below the normal settings of inverse time relays.

S.1.3 When used as a back-up protection for sustained external phase  faults, the selection of the relay and their settings must be very carefully considered. The synchronous impedance ( which will vary anywhere between’   110   to 250   percent  ),   limits   the   sustained    fault    current   fed by the generators to about the same as, or less than, the rated load  current. Due to the rapid decrement of the short-circuit current ( ice Fig. l ), the relay should be so set that it allows sufficient margin over the rated overload capacity of the machine, and, at the same time, is capable of operating at the short-circuit value at full decrement.

    - With an automatic voltage regulator used with machine the sustained fault current would be higher than the maximum load current. In such cares, a simple attracted armature electromagnetic type of overcurrent

°Specification for electrical relays for power system protection.

JRlcctrotechnical vocabulary: Part IX Electrical relays.

| X"d CU | R RE NT |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | 7 OR (II | k v C IR C ui'/ j |  |
|  |  |  |  |  |  | EG UL A |  |  |  |

| NOzz — Voltage regulator In use and ezciter ceiling voltage limited to 1 -35 pu. 0 | 0•5 | T •0 | 1 •5 | 2 0 SE C ONOS |
| --- | --- | --- | --- | --- |
| 0 | 25 | 50 | 7 5 | i 00 C Y C LE S |

Fin.  1	A Tvricac SHORT-Cir curr DEGREh4ENT CURVE

#### relay in conjunction  with  a  definite  time  delay  relay  is  used  to  protect the   generator.    The    overcurrent    setting    may    be    about    125    to 150 percent of the full load current of the generator and the definite timing may be between 3 to 6 secor.ds, depending on the individual case. Sometimes three such units are incorporated, one in each phase of the generator; sometimes only one relay in any one phase, along with a phase unbalance relay is used. Instead of the attracted armature relay with definite time delay, an IDMTI. relay may also be used for a generator with an automatic voltage regulator, and is set at about 120 percent of the full load current of the generator.

    - As a back-up for the unit protection of the generator in case of internal phase faults, the setting mentioned earlier  is quite satisfactory  in cases where the bus-bar fault MVA is appreciably greater than the sustained fault MVA fed by the machine. As a protection against such faults, it is necessary to de-excite the machine by the overcurrent relay.

    - Where generators are  not  fitted  with  automatic  voltage  regulators, the sustained  fault  currents  fed  by  the  generator  on  an  external  fault  may be less than the maximum  load current.  In these  eases,  a  voltage restraint or a voltage controlled inverse time provides the necessary discrimination between generator feeding the normal loads, and the generator feeding zuitained external fault currents. These are dealt with in 3.2 and 3A.

### 6

3•1.7 Overcurrent  relays continue  to  be  used  to prevent  overheating  of

the  generator  rotors  on  account  of  prolonged unbalanced currents.	These

are  described  in  Part  II I  of this guide.	Overcurrent relays interlocked

with the unit protection are also available where the cost current transformers on both sides of the circuit-breaker is

of providing not justified,

for example, when air blast circuit-breakers are used ( ice ebo 3.B).

  - Overcurrent Relay with Voltage Restraint

    - It is an induction disc relay with a voltage restraint circuit which restrains   the  action  of  the  current  element.	The   restraining  coil distin-

guishes  between  a  normal  operating  and  a  short-circuit  condition  by  the

change of voltage even if the magnitudes of currents in the two conditions are equal. The restraining effect is reduced as the voltage drops whenever there is a short-circuit and  the  overcurrent  element  then  operates.  In Fig. 2 time current characteristics of this relay are shown and it may be seen that the sensitivity and speed increase as the voltage restraint decreases. The curves for intermediate values for voltage restraint fall inside the two extremes shown in Fig. 2 but it is better to obtain them from the manu- facturer. Like all other induction overcurrent relays, current taps and time dial arrangement are also provided.

    - It is  recommended  that   current   setting   of   between   200   to 25O  percent  of  the generator  rating  at  rated  voltage  is  selected  if  there is  a  continuously  acting  automatic  voltage  regulator. The  current  setting is reduced to 150 to 200 percent if there  is  no  continuously  acting automatic voltage regulator. The time multiplier  scale  is  chosen  for the zero volt restraint time current characteristic for three-phase  faults close  to the bus-bar. If  the  system  connection  is such  that a  three-phase  fault  on or close to the bus-bar did not produce zero volt restraint on the relay, it is necessary to use an appropriate time current curve for voltage restraint between zero and 11$ volts. In Fig. 3 is shown a generator connected to the bus-bar which  is  feeding  a  radial  circuit. Ordinarily,  it  is quite sufficient to obtain the time and current settings of the relays at C, B and A,  allowing for the co-ordinating  time interval of 0 4 second. The  time of operation  of the back-up relay at A may, however, be reduced if the effect of the decaying current on the performance of the relay at B and A is calculated. A typical decrement curve is shown in Fig. 1.

    - The calculation of the behaviour of relays at A and B on decaying fault current, is ’done by trial and error method. For  details  of  this  method reference is invited to 6.4.3.1 of IS : 3842  ( Part I )-1967•.  To  start with, the time of operation of relay at B is assumed.  Then  the  average current  from  time  zero  to  the  time of operation  of relay  at B is

•Application  guide  for  electrical  relays  for ac  systems:   Part  1  Overcurrent  relays for

feeders and Oansformcrs

IS:]84 (PmmII)-1966

obtained from the decrement curve by step-by-step method. If  the  average current  so  obtained  is  insufficient to  close  the  contacts  of  the  relay  at  Zt, the time of operation of this relay is accordingly raised and the step-by-step method is continued  until  a satisfactory  answer  is obtained.  The  next step is to select a time dial setting for the  relav at  N  to  make it selective  with  relav at B. As may be seen from Fig. 3, that  by taking account  of  the  decrement of the fault current, the operation of the generator relay can  be  made  faster  by about half a second.

3•3 Voltage Ctozztrol1ed Overcurxezzt Retays

J.'I.1 1his reiay teas an intiuction disc overcurrent eiement  with  time  delay operation and an undervoltage element. The two eJeinents are so connected that undervoltage element on operation modifies the characteristic of tire inverse time element, that is, the operating current is reciuced  ñeiow full load current of the machine and the operating time curve is changed to

Fo. 2

REmv

C UR RE NT IN MUL7 IP L E S OF PLU G SE T *ING

TIM EIN  _SI C  ON0 »!

-    -   -    -	115 VOLTS RESTRA!NT

0   YOLT	RESTRAINT

TO-	RELAY	TINE DIAL SETTING

Tm	-CURRENT flHARACTER1STIC CURVES OF OVRRCURREMT

8

#### the standard curve ( set IS : 3231-1965* ) to enable grading under fault conditions to take place more easily. The overcurrent element may be provided with any of the inverse characteristics described earlier, with cur- rent taps and time dial adjustments.  The  relay  may  be set  to  operate  on less than full load current when the voltage falls below a predetermined value.

C T RAT IO • z•00/5

25•/.

FAULT

200 0 MVA

x: 0•055 pu

200/5	600/5

J25"/,	›so •/.

OUSBAR

10 MVA GENERATOR

X’d ° 0 •135 pu x^ d' 0•095 pu

|  | A - 4•5 TN S Z ERO vOLT |  |
| --- | --- | --- |
|  | A- ?•0 T N S REST RAINT |  |
|  | A’— 4•5 T f4 S i0d •k YO L7AGE |  |
|  | RESTR TINT |  |
|  |  | AV E R A GE 5 HO RT - C IR CUIT CURRE N T 0 BTAINE FR0I I DEC RENEUT CU RV E (F ¦ G. l ) T 0 C LOS E |
| SHORT-C IRCUIT C URRE NT AT C |  |  |
| GENERAL OR FU LL- LOAD CURRENT |  | d SHORT C IR C UIT CURRENT AT |

100

1000	1000 0

500

1 00

i0

1•0

01

CURRENT	IN AN PE RES ( BASE D ON 3300 V)

100000

Fio. 3 Co-onninazen True-Cunezirr CURVES OF GzxeRATOR Ovxacunnzx	RzLAYS

9

3.3.2 This relay is a combination of undervoltage and overcurrent  units. The undervoltape relay operates instantaneously but the time current characteristics of the overcurrent unit is  similar  to  that  of  an  IDMTL relay. Figure 4 shows the typical characteristics of a voltage controlled overcurrent relay.  Curve  1  gives  the  time-current  characteristics  for  over- load conditions and curve 2 gives the same characteristics for short-circuit conditions, that is, when the voltage falls on account of the short-circuit.

l

I \ I I I

k II I 1

1 J I

I

C HARAC T E RIS - V OL TA GE )

i i

111

HARACTE RISTIC VOLTAGE )

C W

LT

( LO

WFAU

1111

M

DA D

3RNAL

I - OVE R L

C (

I I I I

1 1 1 I

I

i iui

I J

100

8 0

60

40

OPERATING TIME IN SECOND5

20

10

8•0

6•0

2•0

1•0

0•2	o•t	o•s

i	2	4

t0	20

EU LTlPc E 5 OF PLUG SET TING

Fio.  4    CHAR ACTRRI6TIC:8   OF  VOLTAGE CO2' TROLLR	OVERCURRENT

Relav

3.3.3 Instantaneous undervoltage element controls operation of the induction overcurrent element and should be set to operate at  a  voltage above the minimum value expected under the fa’ult conditions likely to be met on the system. The overcurrent unit is set to ride over the normal load swingi. It should be checked that the voltage at the generator terminals

10

### is sufficient  to  operate  the  undervoltage  element  for  all  external  faults for which the overcurrent relay should  back-up.  This is particularly  rele- vant for a generator-transformer unit connection because the impedance  of the transformer together with the effect of automatic voltage regulator may not produce sufficient voltage drop ( the voltage being taken from the genera- tor voltage transformer ) for a fault just outside the transformer secondary terminals.

3.3.a rhe operating characteristics of this relay do not change with the voltage as it does in the case of overcurrent relays with voltage restraint between zero to rated voltage. On the contrary the relay operates or not according as the voltage is below or above the setting.

3.3.5 An example of’ application of voltage controlled overcurrent relay with definite time characteristic is given in Appendix A.

### 3.4 Ixsterloclced 0 'ercurreat Protectxoa

3.•1.1 Interlocked overcurrent protection is required if all the protective current transformers are located  on  one side of  the circuit-breaker only as shown in Fig. 5. A fault occurring between the circuit-breaker contacts and the current transformers cannot be cleared completely either by the bus-bar protection or the differential protection of the generator. Figurr 5 shows two possible locations of the current transformers. A fault at point A is continued to be fed by the generator even after the circuit-breaker has been opened by bus-bar protection. Similarly, a fault at B, although detected by the generator differential protection, is not cleared by the resultant opening of the circuit-breaker.

3.•1.2 A special overcurrent relay interlocked with either of them depending on the location of the current transformers, is used to isolate the fault completely.  An overcurrent  relay with a sufficient  time  delay  setting is interlocked with the appropriate protection, that is,  bus-bar protection or the differential protection. For a fault at  A, the  tripping  relay  associated with the bus-bar protection  closes  a  normally  open  contact  to  complete the circuit of the shading winding of the  overcurrent  relay  allowing  the latter   to   shut   down   the   generator.   For   a   fault   at    B,   the   tripping   relay of the differential protection completes  the  circuit  of  the shading  winding of the overcurrent relay which in turn operates the  bus-bar  protection tripping relay to clear the faulty section..

3.4.3 Normally these relays are provided with a current setting of about

75 percent of rated current for three-phase faults for a fault at A.  The operatng time of the relay is about 0 4 second at 5 times the current setting. However, the relay settings for fault at B should be carefully selected after ascertaining the fault in-feed frotn the bus-bar side.

3.4.I The relay usually employs an induction di‘sc pattern construction having a summation type of main electromagnet winding ( src Fig. 6 ). The

BREAK E R

-  BUS6AP 5	—O

FAULT A

tE   0  KEN{	""

i? iii â

PROTE CTION RELAY

P ROT ECTION RELAY

D

FAULT B

SA   Fault   on Generator  Slde	SB Fault on Line Slda

Fio.  5	IxTRRLOC2tBD OVER CURRENT PROTECTION

shading circuit consists  of  a  wound  shading  coil,  a  saturating  choke  and a capacitance. The choke is designed so that it  starts  to saturate  juit below the setting current of the relay. This feature gives the relay a high torque near the setting and definite minimum time characteristic. The shading circuit is closed by a normally open contact of the bus-bar or generator differential protection, as the case may be, to make the relay operative.

3.4.5 Instantaneous highset overcurrent relays are used to give high speed tripping on phase faults. The current setting provided is normally continuously variable and the relay is set above the maximum starting cur- rent. Relays with low transient over-reach may be used which can be act very close to  the  maximum  starting  current.  Typical  settings are  800 to 1 600 percent of rated current transformer secondary current.

3J Sett:jags ated Go-ordJoatxozt of Overcuxxeat Relays

#### IDMTL  relays  when  used   are   given   a   setting   between   125 to 200 percent of the rated current depending upon the overload charac- teristics of the generator. These relays are used for back-up protection only when continuously acting automatic voltage regulators  are  provided. Settings depend to a  large  extent  on  whether  operation  on  loss  of field is

required  or  not.	If  it  is  desired  that  the  overcurrent  relay  should not

#### operate on loss of field  then it ii  necessary  to select the current settings such

12

TO GENERATOR TRIP

OPERAS ING COIL TUNED SHADING COIL

Fio.   6	IN THRLOCKB» O V£•R CURRENT PROTECTION R e xv

that it will not operate on the excitation current  drawn  by  the  generator from the system. The grading of these  relays  with  similar  relays  on  the feeders may be worked out on the same r rinciple as outlined in Part I of this guide.

    - Voltage controlled and voltage restraint overcurrent relays are normally provided on machines which are not fitted with automatic voltage regulators and where back-up protection with an overcurrent relay is difficult because the synchronous impedance limits the three-phase fault current on sustained faults to about the same or even less than the maximum load cur- rent. When these relays are used, it is preferable to use similar relays on the bus-bars for the outgoing feeders so that proper and easy grading may be ensured for feeder faults.  Where  a  voltage  restraint  type  of relay is used, the current-time characteristic of  the  relay  is  affected  by  the  voltage,  making it difficult to co-ordinate with other relays on the feeders. Unless carer«lly applied, such relays may also provide grading difficulty when distance relays are used for the feeders. Zone 2 and zone 3 operating time of the distance relays should be less than the operating time of the voltage restraint relays under various fault conditions.

    - Voltage restraint and •oltage on inadvertent loss of voltage supply.

controlled   relayi  can mal-operate

In  order  to  prevent  false tripping

on load, fuse failure relays may be used to supervise the voltage transformer

secondary fuses.

  - The guiding factor for overcurrent relays for motors is that  they should not operate due to the momentary excess currents during the normal starting condition but they should provide adequate protection to the motor during abnormal starting conditions as well as during sustained overloads in running conditions.

  - Usually there are two types of overcurrent relays used for the protection of motors, namely:

    - Thermal rcla ys ( i« IS : 1822 -1967* for relays forming an integral part of motor starters and IS : 3231-1965} for relays  installed separately ), and

    - Induction type relays ( see IS : 3231-1965} ).

  - Instantaneous overcurrent relays having a setting  range  of  about 200 to 800 percent or 400 to 1 600 percent of current transformer secondary current may be used to provide protection against phase faults on the moton. The exact setting of such relays is normally determined at the time of com- missioning. The setting should be high enough to prevent  mal-operation under motor starting conditions.

6.4  For overload  protection  of motors, it  is common  to use  thermal  relays  [ see IS : 384"2 ( Part IV ) - 1966} ]. However, in certain  cases,  overcurrent relays with very inverse and extremely inverse characteristics may also be used. In some applications, both thermal and induction type  overcurrent relays are used to provide complete overload protection to motors, both under light  overloads  and  heavy  overloads. One  such  example  is shown in  Fig.  7.  The  type  ot’  relay  required  depends  on  motor  starting   and thermal withstand characteristic [ see IS : 3842 ( Part IV ) - 19661-I

  - In addition to thermal relays, long time induction disc  relays are  also used for motor protection. However, thermal protection has an  advantage over long time induction disc relays because of the spread between hot and cold  characteristics.  This  allows  a  tripping  time  of  less  than   the  starting time when a hot motor is stalled, so that separate stalling protection is less likely to be necessary. This, of course, depends upon  the starting  conditions of the motor and applies when the motors are not expected to start when hot, that is, thermal relay characteristics  permitting  the  motor  to  start  only when cold. Details regarding application of thermal relays are  covered  in Part IV of this guide.

    - Specification for ac motor starters of voltage not exceeding 1 000 volts (Jrst reeiiton).

}Specificat ion for electrical relays for power syst em prote Ction.

t Application guide for electrical relays for ac systems: Part IV Thermal rel aye.

t0000

6000

*000

i

2000

'

1 00 0

800

-

I'

'

400

E IN SEC ON OS

200

100

8O

60

11

OPERATING

E R M AL

T H WI7

H ST A ND

IA RAC T E RI STI C ” M OT 0 R

TY P

CAL THE C HARAC

Rk\AL F T E RISTI

E L C

6	I N DUC T ION D I SC R E LAY ( EX

M E LY

T RE - TlC )—

6

INVERSE

C HARACT E RI S

2	4	6	t0

CURRENT IN MULTIPL E S OF PE R CE NTAG€ CU R RENT SET TIN 6 IN AM P E RE S

Tio. 1 PROTECTION OF A 480 kW, 3 -3 kV MOTOR USING TxERMAL A ID

INDUCTION  DISc   RE LA YS

### Instantaneous earth fault protection having a setting of about  20 percent of rated current transformer secondary current may also be provided  on motors which are connected to systems earthed through a resistance or reactance. Such relays may be operated in series with a stabilizing resistance to prevent mal-operation under starting.

A P  P E N D I X	A

( Clause  3.3.5 )

EXAwrrn  snore AsArrLICATION  OF  VOLTAGE CONTROLLED OVERCURRENT RELAY WITH DEFINITE TIME CHARACTERISTIC

#### Rated full load  generator  current at  11 kV	= 7 050 A

Current transformer ratio	= 8 000J5	1 600

Relay  drop-out  coesieient	— 0-85

Current setting of  the relay	= where l -25 is the reliability factor.

1-25  x  7 050

0-85  x 1 600

6•5 A,

The voltage setting has been made equal to 70 percent of minimum

operating voltage.

Voltage setting	= 0 7  x  l1  x 10'   = 77  volts,

100

#### where  100  is the  voltage   transformer  ratio   and  11 000  volts  is the

rated voltage.

As the protection is of definite time, it is set to operate after a time lag

of 4 seconds.

After setting the relays as above, a check has also been made regarding the response on three-phase fault at 220 kV bus-bar. It may be mentioned here that in between the 11 kV generator bus-bar  and  the  220  kV  bus-bar,  there is 1 I }220 kV unit transformer.

#### Fault current on 11 kV side for a fault

on  220 kV bus-bar	20 800 A

Current sensitivity

20 800

—	6-5 x l 6(10

#### ratio.

where 6‘5 is the current setting and 1 600 is the current transformer

#### Voltage at 11 kV side for a three-phase

fault at 220 kV bus-bar

Voltage sensitivity

#### 4 3 kV

77 x 100 — l -8

#### $.-3 x 10a

This shows that both the current element as well as the voltage element

#### will operate positively for a fault on 220 kV bus-bar.

16

BUREAU OF INDIAN STANDARDS

Manak Bhavan, 9 Bahadur Shah Zafar Marg, NEW DELHI 110002 Telephones: 323 0131, 323 8375, 323 9402

Fax : 91 11 3234062, 91 11 32ae3es

Plot No. 20/9, Site IV, Sahibabad Industrial Area, Sahibabad 201010

Haglonal Offices:

Telegrams : Manaksanstha (Common to all Offices)

Telephone

8-JT0032

Central : Manak Bhavan, e Bahadur Shah Zafar Marg, NEW DELHI 110002	323 76 17

*Eastern : 1/14 CIT Scheme VII M, V.I.P. Road, Maniktola, CALCUTTA 700054	337 86 62

Northern : SCO 335-336, Sector 34-A, CHANDIGARH 160022	60 38 43

Southern : C.I.T. Campus, IV Cross Road, MADRAS 600113	235 23 15

tWestern : Manakalaya, E9, Behind Marol Telephone Exchange, Andheri (East), B32 s2 es MUMBAI 400093

'Pushpak', Nurmohamed Shaikh Marg, Khanpur, AHMEDABAD 380001 3Peenya Industrial Area, 1st Stage, Bangalore-Tumkur Road,

BANGALORE 56O058

550 13 4e

eae 4s 55

Gangobi Complex, Sth Floor, Bhadbhada Road, T.T. Nagar, BHOPAL 462003	55 40 21

Plot No. 62-63, Unit VI, Ganga Nagar, BHUBANESHWAR 751001	4O 36 27

Kalaikathir Buildings, 670 Avinashi Road, COIMBATORE 641037	21 01 41

Plot No. 43, Sector 16 A, Mathura Road, FARIDABAD 12J001	B-2e 88 01

Savitri Complex, 116 G.T. Road, GHAZIABAD 201001	B-71 19 96 M/5 Ward No.29, R.G. Barua Road, Sth By-lane, GUWAHATI 7B1003	54 11 37

5-8-56C, L.N. Gupta Marg, Nampally Station Road, HYDERABAD 500001	2O 10 83 E-52, Chitaranjan Marg, C-Scheme, JAIPUR 302001	37 Z6 25

117/418 B, Sarvodaya Nagar, KANPUR 208005	21 68 76

Seth   Bhawan,   2nd   Fbor,   Behind   Laela   Cinema,   Naval   Kishore   Road,	23 80 23

LUCKNOW 226001

Pa¥ipuSa Indusbial Estate, PATNA 800013	26 23 05

T.C. No. J4/1421, University P. O. Palayam, THIRUVANANTHAPURAM 605034	6 21 17

/nsp•etfon Dffiaec (With Sale Point) :

Pushpanjali,  1st Floor,  205-A,  West  High  Court  Road,  Shankar Nagar  Square,	52 51 71

NAGPUR 440010

Institution of Engineers (India) Building 1332 Shivaji Nagar, PUNE 411005

°Sales Office is at 5 Chowringhee Approach, P.O. Princep Sbeet CALCUTTA 700072

tsales Office is at Novelty Chambers,”Grant Road, MUMBAI 400007 tsales Offioe is at ’F' Block, Unity Building, Narashima •i• Square,

BANGALORE 56OIXI2

32 36 35

27 10 05

309 65 25

222 89 7J

Reprography Unit, BIS, Mew Delbi, India