Doc : CED 50 (13682)

भारतीय मानक

तप्त और अतप्त पेय जल वितरण व्यवस्था के लिए क्लोरीनीकृत पॉलीविनयल क्लोराइड (सी.पी.वी.सी) फिटिंग - विशिष्टि

Indian Standard

CHLORINATED POLYVINYL CHLORIDE (CPVC)

FITTINGS FOR POTABLE HOT AND COLD WATER

DISTRIBUTION SUPPLIES — SPECIFICATION

ICS 23.040.45; 91.140.60

© BIS 2020

B U R E A U  O F  I N D I A N  S T A N D A R D S

MANAK BHAVAN, 9 BAHADUR SHAH ZAFAR MARG

NEW DELHI 110002

March 2020	     	                                                                                  Price Group

Plastic Piping Systems Sectional Committee, CED 50

FOREWORD

This Indian Standard was adopted by the Bureau of Indian Standards, after the draft finalized by the Plastic Piping Systems Sectional Committee had been approved by the Civil Engineering Division Council.

This Indian standard specifies the characteristics of fittings made from chlorinated polyvinyl chloride (CPVC) for piping system intended for jointing by using solvent cement to CPVC pipes covered by IS 15778:2007 – Chlorinated polyvinyl chloride (CPVC) pipes for potable hot and cold water distribution supplies – Specification.

In the formulation of IS 15778:2007 dealing with CPVC pipes, considerable assistance was derived from the following international standards:

- ISO 15877-1:2009 – ‘Plastics piping systems for hot and cold water installations – Chlorinated poly(vinyl chloride) (PVC-C) – Part 1 : General’,

- ISO 15877-2:2009 – ‘Plastics piping systems for hot and cold water installations – Chlorinated poly(vinyl chloride) (PVC-C) – Part 2 : Pipes’, and

- ASTM D2846 – ‘Standard specification for chlorinated poly(vinyl chloride) (CPVC) plastic hot and cold water distribution systems’.

The sizes of fittings have been kept as per the practice followed by the CPVC pipe manufacturers in India.   All the tests have been covered as per the corresponding ISO standard for the CPVC fittings, that is, ISO 15877: 3 'Plastic piping system for hot and cold water distribution – Chlorinated Poly Vinyl Chloride (PVC-C) – Part 3: Fittings'.

In this standard, the dimensions of the fittings have been provided in a manner to meet the requirements of CPVC pipes as given under Table 2 of IS 15778:2007.

The standard covers SDR 11 and SDR 17 fittings, however, IS 15778 covers SDR 13.5 pipes also apart from SDR 11 and SDR 17 pipes.  Thus, fittings for SDR 13.5 pipes are not covered in this standard.   The SDR 11 fittings can be used for SDR 13.5 pipes as well with higher factor of safety.

This standard does not purport to address all the safety problems associated with its use. It is responsibility of the users of this standard to establish appropriate safety and health practices and determine the applicability of regulatory safety and health practices and determine the applicability of regulatory limitation prior to use.

The composition of the technical committee responsible for formulation of this standard is given in Annex C.

For the purpose of deciding whether a particular requirement of this standard is complied with the final value, observed or calculated, expressing the result of a test or analysis, shall be rounded off in accordance with IS 2 : 1960 ‘Rules for rounding off numerical values (revised)’. The number of significant places retained in the rounded off value should be the same as that of specified value in this standard.

Doc: CED 50 (13682)

Indian Standard

CHLORINATED POLYVINYL CHLORIDE (CPVC)

FITTINGS FOR POTABLE HOT AND COLD WATER

DISTRIBUTION SUPPLIES — SPECIFICATION

1 SCOPE

This standard specifies requirements regarding material, test methods, inspection and marking of injection moulded chlorinated polyvinyl chloride (CPVC) fittings for hot and cold water distribution supplies for water service up to and including 82 °C, intended for connection by using solvent cement to CPVC pipes covered by IS 15778. This standard is applicable to fittings of following types:

- Fittings with solvent cemented joints;

- Mechanical fittings; and

- Fittings with incorporated inserts.

2  REFERENCES

The standards listed in Annex A contain provisions, which through reference in this text constitute provisions of this standard. At the time of publication the editions indicated were valid. All standards are subject to revision and parties to agreements based on this standard are encouraged to investigate the possibility of applying the most recent editions of the standard indicated in Annex A.

3  TERMINOLOGY

For the purpose of this standard, the following definitions shall apply.

3.1 Nominal Size (DN) ― The numerical designation for the size of a fitting, other than a fitting designated by thread size, which is a convenient round number approximately equal to the manufacturing dimensions in millimeters.

3.2 Mean Inside Diameter of Socket at Entry (ds1) ― Arithmetic mean of two measured inside diameters perpendicular to each other at the entry of socket.

3.3 Mean Inside Diameter of Socket at Shoulder (Bottom) (ds2) ― Arithmetic mean of two measured inside diameters perpendicular to each other at the shoulder (bottom) of socket.

3.4 Out-of-Roundness (Ovality) ― Difference between the measured maximum inside diameter and the measured minimum inside diameter in the same cross sectional plane of a socket.

3.5 Minimum Wall Thickness (emin) ― The minimum value of the measurement of the wall thickness at any point around the circumference of the component.

3.6 Tolerance ― The permitted variations of the specified value of a quantity, expressed as the difference between the permitted maximum and the permitted minimum values.

3.7 Working Pressure (PN) ― The numerical designation of a fitting related to the mechanical characteristics of that fitting used for reference purposes.

3.8 Tests

3.8.1 Type Tests ― Tests carried out whenever a change is made in the composition or in the size in order to establish the suitability and the performance capability of the fitting.

3.8.2 Acceptance Tests ― Tests carried out on samples taken from a lot for the purpose of acceptance of the lot.

3.9 Virgin Material ― Material in such form as granules or powder that has not been subjected to use or processing other than that required for its manufacture and to which no re-processible or recyclable material(s) have been added.

3.10 Own Rework Material ― Material prepared from rejected unused fittings, including the runners from the production of fitting, which will be reprocessed in a manufacturer’s plant by a process such as injection moulding, and for which the complete formulation is known.

3.11 Fittings for Solvent Cement Joint ― Fitting in which the joint with the pipe or another component is made by means of an adhesive.

3.12 Mechanical Fittings

3.12.1 Compression Fitting ― Fitting in which the joint is made by the compression of a ring or sleeve on the outside wall of the pipe with or without additional sealing elements and with internal support.

3.12.2 Flanged Fittings ― Fitting in which the pipe connection consists of two mating flanges, which are mechanically pressed together and sealed by the compression of an elastomeric sealing elements between them.

3.12.3 Flat Seat Union Fitting ― Fitting in which the pipe connection consists primarily of two components, at least one which normally incorporates a flat sealing surface, which are mechanically pressed together by means of a screwed nut or similar and sealed by the compression of an elastomeric sealing element between them.

3.12.4 Fitting with Incorporated Inserts ― Fitting in which the joint is made by means of connecting threads or other outlets, inserted in the injection-moulded fitting body, combined with at least one solvent cement socket injection-moulded fitting body, combined with at least one solvent socket.

4  NOTATION

The following notation (symbols) shall apply in this standard:

| DN | = | nominal size |
| --- | --- | --- |
| ds1 | = | Inside diameter of the socket at entry (at mouth) |
| ds2 | = | Inside diameter of the socket at shoulder (at root/ bottom) |
| d1 | = | nominal diameter of the socket |
| d2 | = | nominal diameter of the spigot |
| D | = | inside diameter at mid-point of socket length |
| L | = | socket length |
| l0 | = | free length |
| r | = | bending radius |
| αn | = | nominal angle of fitting (total included angle of taper) |
| eds1 | = | minimum wall thickness at socket entry |
| eds2 | = | minimum wall thickness at socket shoulder (bottom) |
| eo | = | minimum wall thickness overall wall |
| PN | = | nominal pressure (working pressure) |
| fT | = | de-rating factor for water temperatures |
| ρ | = | material density |
| σ | = | hydrostatic stress |
| σs | = | Design stress |
| X | = | Outside Diameter |

5  CLASSIFICATION OF FITTINGS

The fittings shall be classified on the basis of pressure rating (working pressure) at 27 °C and 82 °C shall be as given in Table 1.

Table 1 Classification of Fittings Based on Pressure Rating

(Clause 5)

| Sl No. | SDR | Size mm (inches) | Working Pressure MPa |  |
| --- | --- | --- | --- | --- |
|  |  |  | 27 °C | 82 °C |
| (1) | (2) | (3) | (4) | (5) |
|  | 11 | 15 to 50 (½” to 2”) | 2.76 | 0.68 |
|  | 17 | 65 to 150 (2-½” to 6”) | 1.73 | 0.42 |
| NOTE ꟷ The above fittings are recommended for water temperature ranging from +1 to +82 °C. The recommended maximum safe working stress for these fittings is 13.8 MPa at 27 °C. At higher temperature up to 82 °C, the strength of the fitting reduces and the working pressure shall be modified in accordance with Fig. 1 of IS 15778. Occasional rise in temperature as in summer season with concurrent corresponding reduction in temperature during nights has no deleterious effect on the life/working pressure of the fittings considering the total life of fittings. |  |  |  |  |

6  COMPOSITION

6.1 The compound from which the fitting is produced shall consist substantially of chlorinated polyvinyl chloride to which may be added only those additives that are needed to facilitate the manufacture of the fitting and the production of sound and durable fitting of good surface finish, mechanical strength and opacity under conditions of use. None of these additives shall be used separately or together in quantities sufficient to constitute a toxic, organoleptic or microbial growth hazard or materially to impair the fabrication, or to impair the chemical, physical or mechanical properties (in particular long-term mechanical strength and impact strength) as defined in this standard.

6.2 Compound Properties

6.2.1 The chlorinated polyvinyl chloride compound used for the manufacture of fittings shall meet the requirements of grade G.I.103-2-3-2 of IS 15225.  It shall have minimum performance designation of, as per designation system given in 4.2 of IS 15225.

6.2.2 Compound Chlorine Content

The chlorinated polyvinyl chloride fittings compounds containing additives such as modifiers, lubricants, fillers, etc, from which the fittings are to be manufactured, shall have chlorine content not less than 55 percent when tested in accordance with Annex B of IS 15778.

6.2.3  The additives to be used for the manufacture of compound shall be selected from IS 10148 and shall be uniformly dispersed.  There shall be no deliberate addition of lead or lead compound in the resin (see Note).

NOTE —  Any statutory rules/regulations for phasing out of use of lead stabilizers in plastic pipes and fittings shall be referred and complied to accordingly.

6.2.4 Density

The chlorinated polyvinyl chloride fittings compounds containing additives such as modifiers, lubricants, fillers, etc, from which the fittings are to be manufactured, shall have a density between 1 450 kg/m3 and 1 650 kg/m3, when tested in accordance with IS 13360 (Part 3/Sec 10) and IS 13360 (Part 3/Sec 11).

6.2.5 Verification of the Malfunction Temperature, Tmal

When tested as per the method given in Annex C of IS 15778, at 95 ± 2 °C and a test pressure of 1.0 MPa for 1 000 h, the fittings shall not leak during the prescribed test duration.

7  DIMENSIONS OF FITTINGS

7.1  Diameter

The inside diameter of the socket at entry and the inside diameter of the socket at shoulder (bottom), when measured in accordance with IS 12235 (Part 1) shall be as given in Table 2.  The outside diameter of reducer bushing shall be as given in Table 3.

7.2 Wall Thickness

The wall thicknesses of the socket at entry and shoulder, when measured in accordance with IS 12235 (Part 1) shall be as given in Table 2.

7.3 The socket length, ovality of the socket at entry and shoulder, inside diameter at the mid-point of socket length (D) and EW, EX and EZ, when measured in accordance with IS 12235 (Part 1) shall be as given in Table 2.

| Table 2 Dimensions of Inside Diameter of the Socket at Entry and Shoulder, Socket Length, Inside Diameter and Wall Thickness (Clauses 7.1, 7.2 and 7.3) All Dimensions in millimetres. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sl No. | Nominal Fitting Size mm (inches) | Inside diameter of the socket at entry, ds1 |  |  | Inside diameter of the socket at shoulder (bottom), ds2 |  |  | Socket Length, L (min) | Inside Diameter, D (min) | Wall Thickness, min |  |  | Entrance, EW EX, EZ (min) |
|  |  | Diameter mm | Tolerance on Nominal Diameter | Maximum Out-of-Round | Diameter | Tolerance on Nominal Diameter | Maximum Out-of-Round |  |  | Socket at Entry eds1 | Socket at Shoulder eds2 | eo |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) |
| i) | SDR 11 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 (1/2”) | 16.08 | ± 0.08 | 0.20 | 15.72 | ± 0.08 | 0.20 | 12.70 | 12.42 | 1.73 | 2.59 | 3.25 | 0.86 |
|  | 20 (3/4”) | 22.45 | ± 0.08 | 0.26 | 22.10 | ± 0.08 | 0.26 | 17.78 | 18.16 | 2.03 | 2.59 | 3.25 | 0.86 |
|  | 25 (1”) | 28.83 | ± 0.08 | 0.30 | 28.47 | ± 0.08 | 0.30 | 22.86 | 23.39 | 2.59 | 2.59 | 3.25 | 0.86 |
|  | 32 (1-1/4”) | 35.20 | ± 0.08 | 0.36 | 34.85 | ± 0.08 | 0.36 | 27.94 | 28.58 | 3.18 | 3.18 | 3.96 | 1.07 |
|  | 40 (1-1/2”) | 41.66 | ± 0.10 | 0.40 | 41.20 | ± 0.10 | 0.40 | 33.02 | 33.76 | 3.76 | 3.76 | 4.70 | 1.24 |
|  | 50 (2”) | 54.38 | ± 0.10 | 0.50 | 53.92 | ± 0.10 | 0.50 | 43.18 | 44.17 | 4.90 | 4.90 | 6.12 | 1.63 |
| ii) | SDR 17 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 65 (2-1/2”) | 73.38 | ± 0.18 | 0.76 | 72.85 | ± 0.18 | 0.76 | 44.45 | 57.15 | 6.88 | 6.88 | 8.76 | EW 2.3, EX, EZ 3.3 |
|  | 80 (3”) | 89.31 | ± 0.20 | 0.76 | 88.70 | ± 0.20 | 0.76 | 47.63 | 71.63 | 7.47 | 7.47 | 9.53 | EW 2.3, EX, EZ 3.3 |
|  | 100 (4”) | 114.76 | ± 0.23 | 0.76 | 114.07 | ± 0.23 | 0.76 | 57.15 | 94.92 | 8.40 | 8.40 | 10.67 | EW 2.3, EX, EZ 3.3 |
|  | 150 (6”) | 168.83 | ± 0.28 | 1.52 | 168.00 | ± 0.28 | 1.52 | 76.20 | 143.41 | 10.76 | 10.76 | 13.72 | EW 3.3,EX, EZ 4.8 |
| NOTES 1 In plastic to metal fittings, dimensions of sockets at plastic side should be as per this table and dimensions at metal side should be as per manufacturer’s specification. 2 EW, EX and EZ dimensions are only for guideline. |  |  |  |  |  |  |  |  |  |  |  |  |  |

Table 3 Dimensions of Reducer Bushing or Coupling CPVC Socket Type Pipe Fitting

(Clause 7.1)

All dimensions are in millimetres.

| Sl No. | Nominal Size | Outside Diameter, X |
| --- | --- | --- |
| (1) | (2) | (3) |
|  | 20 mm (3/4”) X 15 mm (1/2”) | 22.1 to 22.3 |
|  | 25 mm (1”) X 15 mm (1/2”), 25 mm (1”) X 20 mm (3/4”) | 28.5 to 28.7 |
|  | 32 mm (1-1/4”) X 15 mm (1/2”), 32 mm (1-1/4”) X 20 mm (3/4”), 32 mm (1-1/4”) X 25 mm (1”) | 34.8 to 35.0 |
|  | 40 mm (1-1/2”) X 15 mm (1/2”), 40 mm (1-1/2”) X 20 mm (3/4”), 40 mm (1-1/2”) X 25 mm (1”), 40 mm (1-1/2”) X 32 mm (1-1/4”) | 41.2 to 41.4 |
|  | 50 mm (2”) X 15 mm (1/2”), 50 mm (2”) X 20 mm (3/4”), 50 mm (2”) X 25 mm (1”), 50 mm (2”) X 32 mm (1-1/4”), 50 mm (2”) X 40 mm (1-1/2”) | 53.9 to 54.1 |
|  | 65 mm (2-1/2”) X 32 mm (1-1/4”) , 65 mm (2-1/2”) X 40mm (1-1/2”) , 65 mm (2-1/2”) X 50 mm (2”) | 72.8 to 73.2 |
|  | 80 mm (3”) X 50 mm (2”), 80 mm (3”) X 65 mm (2-1/2”) | 88.7 to 89.1 |
|  | 100 mm (4”) X 50 mm (2”), 100 mm (4”) X 65 mm (2-1/2”), 100 mm (4”) X 80 mm (3”) | 114.1 to 114.5 |
|  | 150 mm (6”) X 50 mm (2”), 150 mm (6”) X 65 mm (2-1/2”), 150 mm (6”) X 80 mm (3”), 150 mm (6”) X 100 mm (4”) | 168.0 to 168.6 |
| NOTE — Tubing socket dimensions, ds1, ds2 and L, and tolerances on these dimensions shall be the same as those in Table 2. The minimum length of the male end of the bushing or coupling, LM, shall be the same as L in Table 2, but in any case the male end shall bottom in the mating fitting. Minimum waterway dimensions, D shall be the same as D in Table 2. |  |  |

8 PHYSICAL AND CHEMICAL CHARACTERISTICS

8.1 Visual Appearance

The colour of the fitting shall be off-white.

NOTE — Slight variations in the appearance of the colour are permitted.

8.1.1 When viewed without magnification, the internal and external surfaces of fittings shall be smooth, clean and free from scouring, cavities and other surface defects to an extent that would prevent conformance with this standard. The material shall not contain visible impurities.

8.2 Opacity

The wall of the plain fitting shall not transmit more than 0.2 percent of the visible light falling on it when tested in accordance with IS 12235 (Part 3).

8.3 Stress Relief Test

The test specimen shall not show blisters, excessive delamination or cracking or signs of weld line splitting when tested in accordance with IS 12235 (Part 6). The weld line or lines may become pronounced during the test, but this shall not be deemed to constitute failure.

8.4 Vicat Softening Temperature

When tested by the method prescribed in IS 12235 (Part 2), the Vicat softening temperature of the specimen shall not be less than 103 C.

8.5 Density

When tested in accordance with IS 12235 (Part 14), the density of the fittings shall be between 1 450 kg/m3 and 1 650 kg/m3.

8.6 Effect on Water

The fittings shall not have any detrimental effect on the composition of water flowing through them. The fittings when tested in accordance with the methods given IS 12235 (Part 4), IS 12235 (Part 10) and IS 12235 (Part 11), the quantities of lead, dialkyl tin C4 and higher homologues (measured as tin), and any other toxic substances extracted from the internal walls of the fittings in the test solution shall not exceed the concentrations as specified in 10.3 of IS 4985.

NOTE — The phase out programme for use of lead stabilizers in PVC pipe manufacturing being implemented by the concerned statutory Authority shall be borne in mind.

9 MECHANICAL PROPERTIES

9.1 Hydrostatic Characteristics

When subjected to internal hydrostatic pressure test in accordance with the procedure given in IS 12235 (Part 8/Sec 1), the fitting shall not fail during the prescribed test duration. The temperatures, duration and hydrostatic (hoop) stress for the test shall conform to the requirements given in Table 4. The test shall be carried out not earlier than 24 h after the fittings have been manufactured.

Fittings can be tested either as fitting with mechanical sealed end caps or as an assembly with pipes.

When tested as an assembly, the fittings shall be connected to the corresponding pipe conforming to IS 15778, either by using solvent cement or joined by a mechanical assembly, in such a way that the required hydrostatic test pressure given in Table 4, can be applied. The free length of the solvent-cemented pipe sections shall be chosen according to IS 12235 (Part 8/Sec 1) in such a way that the axial forces caused by the internal pressure are transferred to the fitting.

Before testing, proper cure time has to be provided to the assemblies based on the recommendation of the manufacturer.

9.2 Thermal Stability by Hydrostatic Pressure Testing

When subjected to internal hydrostatic pressure test in accordance with the procedure given in IS 12235 (Part 8/Sec 1), and as per the requirement given in SI No. (iv) of Table 4, the fitting shall not burst or leak during the prescribed test duration.

Table 4 Requirements of fittings for Internal Hydrostatic Pressure Test

(Clause 9.1 and 9.2)

| Sl No. | Test | Test Temperature °C | Test Period, Min h | Test Pressure MPa |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | SDR 11 | SDR 17 |  |
|  |  |  |  | (5) | (6) |  |
| Hydrostatic Characteristics |  |  |  |  |  |  |
|  | Acceptance | 27 | 1 | 8.62 |  | 5.36 |
|  | Type | 95 | 165 | 1.12 |  | 0.7 |
|  | Type | 95 | 1 000 | 0.92 |  | 0.57 |
| Test for Thermal Stability |  |  |  |  |  |  |
|  | Type | 95 | 8 760 | 0.72 |  | 0.45 |

10 SAMPLING AND CRITERIA FOR CONFORMITY

The sampling procedure and criteria for conformity shall be as given in Annex B.

11 MARKING

11.1 Marking elements shall be printed or formed directly on the fitting in such a way that after storage, handling, and installation, legibility is maintained.

NOTE ― The manufacturer is not responsible for marking being illegible due to actions such as painting, scratching, covering of the components or by use of detergent, etc, on the components unless agreed or specified by the manufacturer.

11.2 Marking shall not initiate cracks or other types of defects which adversely influence the performance of the fitting. If printing is used, the colouring of the printed information shall differ from the basic colouring of the fitting. The size of the marking shall be such that the marking is legible without magnification.

11.3 The marking on the fittings shall show the following:

a) Manufacturer’s name or trademark;

b) Nominal fitting size;

c) Pressure rating of fitting;

d)  SDR of fitting; and

e) The word “CPVC”.

11.3.1 The information regarding batch or lot number, shall be printed on the box or packet containing the fittings.

11.3.1.1 The lot number/batch number shall include the details of production in the following manner:

| Year | Month | Day | Machine No. | Shift |  |
| --- | --- | --- | --- | --- | --- |
| xxxx | xx | xx | xxx | x |  |

11.2 BIS Certification Marking

11.2.1 Each fitting conforming to the requirements of this standard may be certified as per the conformity assessment schemes under the provisions of the Bureau of Indian Standards Act, 2016 and the Rules and Regulations framed thereunder, and the fitting may be marked with the Standard Mark.’

ANNEX A

(Clause  2)

## LIST OF REFERRED INDIAN STANDARDS

| # IS No. | # Title |
| --- | --- |
| 4905 : 2015 | Random sampling and randomization procedures (first revision) |
| 4985 : 2000 | Unplasticised PVC pipes for potable water supplies - Specification (third revision) |
| # 12235 | # Thermoplastics pipes and fittings - Methods of test (first revision) |
| # Part 1 : 2004 | # Measurement of dimensions |
| # Part 2 : 2004 | # Determination of vicat softening temperature |
| # Part 3 : 2004 | # Test for opacity |
| # Part 4 : 2004 | # Determining the detrimental effect on the composition of water |
| # Part 6 : 2004 | # Stress relief test |
| # Part 8/Sec 1: 2004 | # Resistance to internal hydrostatic pressure: Section 1 Resistance to internal hydrostatic pressure at constant internal water pressure |
| # Part 10 : 2004 | # Determination of organotin as tin aqueous solution |
| # Part 11 : 2004 | # Resistance to dichloromethane at specified temperature |
| # Part 14 : 2004 | # Determination of density/relative density (specific gravity) |
| # 13360 | # Plastics – Methods of testing |
| # Part 3/Sec 10):2016 | # Physical and dimensional properties: Section 10 Determination of density of non-cellular plastics – Immersion method liquid pyknometer method and titration method |
| # Part 3/Sec 11):2016 | # Physical and dimensional properties: Section 11 Determination of density of non-cellular plastics – Density gradient column method |
| # 15225 : 2002 | # Chlorinated polyvinyl chloride compounds used for pipes and fittings - Specification |
| # 15778 : 2007 | # Chlorinated poly vinyl chloride (CPVC) pipes for potable hot and cold water distribution supplies – Specification |
| # 10148 : 1982 | # Positive list of constituents of polyvinyl chloride (PVC) and its copolymers in contact with foodstuffs, pharmaceuticals and drinking water |

ANNEX B

(Clause 10)

### SAMPLING AND CRITERIA FOR CONFORMITY

B-1 TYPE TESTS

B-1.1 Type tests are intended to prove the suitability and performance of a new composition, or a new compound (say source) or processing techniques or a new design or size of fitting.  Such tests, therefore, need to be applied only when a change is made in polymer composition or when a new size of fitting is be introduced.

For the purpose of this standard, type tests shall be carried out as per B-1.2 to B-1.7.

B-1.2 Performance Designation and Chlorine Content

For this test, the manufacturer or the supplier shall furnish to the testing authority one sample of the fitting of any size or CPVC compound (whichever is applicable) as mentioned in 6.

B-1.2.1 The sample so selected shall be tested for compliance with requirements for performance designation as mentioned in 6.3.1 and chlorine content as mentioned in 6.3.2.

B-1.2.2 If the sample passes the requirements of the test, the designation of the fitting under consideration shall be considered to be eligible for approval, which shall be valid for a period of one year.

B-1.2.3 In case the sample fails in the test, the testing authority, at its discretion, may call for a fresh sample and subject the same to test.  If the sample passes the repeat test, the class of fitting under consideration shall be considered eligible for approval.  If the sample fails in the repeat test, the type of fitting shall not be approved.  The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

B-1.2.4 At the end of the validity period (normally one year) or earlier, if necessary, the testing authority may call for a fresh sample for test for the purpose of type approval.

B-1.3 Opacity

For this test, the manufacturer or the supplier shall furnish to the testing authority three samples taken at random from the smallest size and lowest pressure rating of the fitting (that is fitting of thinnest wall section), selected at random preferably from a regular production lot.

B-1.3.1 The samples so selected shall be tested for compliance with requirements for opacity as given in 8.2.

B-1.3.2 If all three samples pass the requirements of test, the type of the fitting under consideration shall be considered to be eligible for approval, which shall be normally valid for a period of one year.

B-1.3.3 In case any of the samples fails in the test, the testing authority, at its discretion, may call for fresh samples not exceeding the original number, and subject them to the malfunction test.  If, in the repeat test, no single failure occurs, the type of fitting under consideration shall be considered eligible for type approval.  If any of the samples fails in the repeat test, the type of fitting shall not be approved.  The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

B-1.3.4 At the end of the validity period (normally one year) or earlier, if necessary, the testing authority may call for a fresh sample for opacity test for the purpose of type approval.

B-1.4 Verification of Malfunction Temperature Tmal

B-1.4.1 For this test, the manufacturer or the supplier shall furnish to the testing authority one assembly, selected at random preferably from regular production lot.

B-1.4.2 The sample so selected shall be tested for compliance with requirements for malfunction temperature as given in 6.3.4.

B-1.4.3 If the sample passes the requirements of the test, the type of the fitting under consideration shall be considered to be eligible for approval, which shall be normally valid for a period of three years.

B-1.4.4 In case the sample fails in the test, the testing authority, at its discretion, may call for a fresh sample and subject the same to the malfunction test.  If the sample passes the repeat test, the type of fitting under consideration shall be considered eligible for approval.  If the sample fails in the repeat test, the type of fitting shall not be approved.  The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

B-1.4.5 At the end of the validity period (normally three years) or earlier, if necessary, the testing authority may call for a fresh sample for malfunction test for the purpose of type approval.

B-1.5 Thermal stability test (By Internal Hydrostatic Pressure Test)

B-1.5.1 For this test, the manufacturer or the supplier shall furnish to the testing authority three samples of fittings (any size), selected at random preferably from regular production lot.

B-1.5.2 The samples so selected shall be tested for compliance with requirements for thermal stability test as given in 9.2.

B-1.5.3 If all the three samples pass the requirements of the test, the type of fitting under consideration shall be considered to be eligible for type approval, which shall be normally valid for a period of three years.

B-1.5.4 In case any of the samples fails in this test, the testing authority, at its discretion, may call for fresh samples not exceeding the original number, and subject them to the thermal stability test.  If, in the repeat test, no single failure occurs, the type of fitting shall be considered eligible for type approval.  If any of the samples fails in the repeat test, the type of fitting shall not be approved.  The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

B-1.5.5 At the end of the validity period (normally three years) or earlier, if necessary, the testing authority may call for a fresh sample for thermal stability test for the purpose of type approval.

B-1.6 Internal Hydrostatic Pressure Test (Test Duration 165 h)

B-1.5.1 For this test, the manufacturer or the supplier shall furnish to the testing authority three samples of fittings of same rating and different sizes (including largest and smallest fitting sizes being considered for qualification), selected at random preferably from regular production lot.

B-1.5.2 The samples so selected shall be tested for compliance with requirements for internal hydrostatic pressure test (165 h) as per 9.1 for the test parameters as per Sl. No. (ii) of Table 4.

B-1.5.3 If all the three samples pass the requirements of the test, the type of fitting under consideration shall be considered to be eligible for type approval, which shall be normally valid for a period of two years.

B-1.5.4 In case any of the samples fails in this test, the testing authority, at its discretion, may call for fresh samples not exceeding the original number, and subject them to the internal hydrostatic pressure test (165 h).  If, in the repeat test, no single failure occurs, the type of fitting shall be considered eligible for type approval.  If any of the samples fails in the repeat test, the type of fitting shall not be approved.  The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

B-1.5.5 At the end of the validity period (normally two years) or earlier, if necessary, the testing authority may call for a fresh sample for thermal stability test for the purpose of type approval.

B-1.7 Internal Hydrostatic Pressure Test (Test Duration 1 000 h)

B-1.5.1 For this test, the manufacturer or the supplier shall furnish to the testing authority three samples of fittings of same rating and different sizes (including largest and smallest fitting sizes being considered for qualification), selected at random preferably from regular production lot.

B-1.5.2 The samples so selected shall be tested for compliance with requirements for internal hydrostatic pressure test (1 000 h) as per 9.1 for the test parameters as per Sl. No. (iii) of Table 4.

B-1.5.3 If all the three samples pass the requirements of the test, the type of fitting under consideration shall be considered to be eligible for type approval, which shall be normally valid for a period of three years.

B-1.5.4 In case any of the samples fails in this test, the testing authority, at its discretion, may call for fresh samples not exceeding the original number, and subject them to the internal hydrostatic pressure test (1 000 h).  If, in the repeat test, no single failure occurs, the type of fitting shall be considered eligible for type approval.  If any of the samples fails in the repeat test, the type of fitting shall not be approved.  The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

B-1.5.5 At the end of the validity period (normally three years) or earlier, if necessary, the testing authority may call for a fresh sample for thermal stability test for the purpose of type approval.

B-1.8 Test for Effect on Water

B-1.7.1 For this type test, the manufacturer or the supplier shall furnish to the testing authority three samples of the smallest size fitting from each machine selected at random preferably from a regular production lot.

B-1.7.2 The samples so selected shall be tested for compliance with requirements for effect on water test as given in 8.6.

B-1.7.3 At the end of the validity period (normally one year) or earlier, if necessary, the testing authority may call for fresh samples for type test for the purpose of type approval.

B-2 ACCEPTANCE TESTS

Acceptance tests are carried out on samples selected from a lot for the purpose of acceptance of the lot.

B-2.1 Lot

In a single consignment, all CPVC fittings of the same size, same pressure rating and same SDR, and fabricated under essentially similar conditions shall be grouped together to constitute a lot.

B-2.2 The conformity of the lot to the requirement of this specification shall be ascertained for each lot separately. The number of socket fittings to be sampled from each lot shall depend on the size of lot and shall be in accordance with col 2 and 3 of Table 5.

B-2.2.1 These fittings shall be selected from the lot at random.  In order to ensure the randomness of selection, procedure given in IS 4905 may be followed.

B-2.3 Number of Test and Criteria for Conformity

B-2.3.1 Each socket fitting so selected shall be examined for requirement given in 7 and Sl No. (i) of Table 4 under 9.1.  Any socket fitting failing in one or more of these requirements shall be considered as defective. The lot shall be considered as conforming to the requirement of this specification if the number of defective socket fitting found in the sample does not exceed the corresponding acceptance number A given in col 4 of Table 5.

B-2.3.2 The lot rejected according to B-2.3.1 may be retested for characteristics for which it has failed.  For this purpose, number of socket fittings to be selected at random from the lot shall be according to col 2 and col 3 of the Table 5.  A socket fitting failing to satisfy the requirements of these characteristics shall be considered as defective.  The lot shall be deemed to satisfy the requirements of this specification if the number of defective socket fitting found in the sample does not exceed the corresponding acceptance number B given in col 5 of Table 3, otherwise the lot shall be rejected.

## B-2.4 Visual & Dimensional Requirements

B-2.4.1 The number of test samples to be taken from a lot shall depend on the size of the lot and the outside diameter of the fittings, and shall be in accordance with Table 5.

B-2.4.2 These fittings shall be selected at random from the lot and in order to ensure the randomness of selection, a random number table shall be used.  For guidance and use of random number tables, IS 4905 may be referred to.  In the absence of a random number table, the following procedure may be adopted:

Starting from any fittings in the lot, count them as 1, 2, 3, etc, up to r and so on, where r is the integral part of N/n, N being the number of fittings in the lot, and n the number of fittings in the sample.  Every rth fitting so counted shall be withdrawn so as to constitute the required sample size.

B-2.4.3 The number of fittings given for the first sample in col 4 of Table 5, shall be taken from the lot and examined for visual and dimensional requirements as given in 7 and 8.1 of this specification. A fitting failing to satisfy any of these requirements shall be considered as defective. The lot shall be deemed to have satisfied these requirements, if the number of defectives found in the first sample is less than or equal to the corresponding acceptance number given in column 6 of Table 5. The lot shall be deemed not to have met these requirements, if the number of defectives found in the first sample is greater than or equal to the corresponding rejection number given in col 7 of Table 5. If, however, the number of defectives found in the first sample lies between the corresponding acceptance and rejection numbers given in col 6 and col 7, a second sample of the size given in col 4 shall be taken and examined for these requirements. The lot shall be considered to have satisfied these requirements if the cumulative sample is less than or equal to the corresponding acceptance number given in col 6, otherwise not.

Table 5 Scale of Sampling for Visual

Appearance and Dimensional Requirements

(Clauses B-2.4.1 and B-2.4.3)

| Sl No. | Number of Fitting in the Lot | Sample Number | Sample Size | Cumulative Sample | Acceptance Number | Rejection Number |
| --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) |
| i) | Up to 1 000 | First | 13 | 13 | 0 | 2 |
|  |  | Second | 13 | 26 | 1 | 2 |
| ii) | 1 001 to 3 000 | First | 20 | 20 | 0 | 2 |
|  |  | Second | 20 | 40 | 1 | 2 |
| iii) | 3 001 to 10 000 | First | 32 | 32 | 0 | 3 |
|  |  | Second | 32 | 64 | 3 | 4 |
| iv) | 10 001 and above | First | 50 | 50 | 1 | 4 |
|  |  | Second | 50 | 100 | 4 | 5 |

# B-2.5 Stress Relief Test

B-2.5.1 The lot, having satisfied visual and dimensional requirements, shall be tested for stress relief test as given in 8.3.

B-2.5.2 For this purpose, the number of fittings given for the first sample in col 4 of Table 6 shall be taken from the lot.  The sample fitting failing the stress relief test shall be considered as defective.  The lot shall be deemed to have met the requirements given in this specification for the Stress Relief Test, if the number of defectives found in the first sample is less than or equal to the corresponding acceptance number given in column 6.  This lot shall be deemed not to have met these requirements, if the number of defectives found in the first sample is greater than or equal to the corresponding rejection number given in column 7.  If, however, the number of defectives in the first sample lies between the corresponding acceptance and rejection numbers given in column 6 and column 7, a second sample of size given in column 4 shall be taken and examined for the requirement.  The lot shall be considered to have satisfied the requirements, if the number of defectives found in the cumulative sample is less than or equal to the corresponding acceptance number given in column 6, otherwise not.

# B-2.6 Vicat Softening Test

B-2.6.1 The lot, having satisfied visual and dimensional requirements shall be tested for Vicat softening temperature as given in 8.4.

B-2.6.2 For this purpose, the procedure adopted for sampling and criteria for conformity shall be the same as that for stress relief test under B-2.5.2 using Table 6.

# B-2.7 Density

B-2.7.1 The lot, having satisfied the visual and dimensional requirements, shall be tested for density as given in 8.5.

B-2.7.2 For this purpose, the procedure adopted for sampling and criteria for conformity shall be the same as that for stress relief test under B-2.5.2 using Table 6.

Table 6 Scale of Sampling for Stress Relief,

Vicat Softening Temperature and Density Test

(Clauses B-2.5.2, B-2.6.2 and B-2.7.2)

| Sl No. | Number of Fitting in the Lot | Sample Number | Sample Size | Cumulative Sample Size | Acceptance Number | Rejection Number |
| --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) |
| i) | Up to 1000 | First | 5 | 5 | 0 | 2 |
|  |  | Second | 5 | 10 | 1 | 2 |
| ii) | 1001 to 3000 | First | 8 | 8 | 0 | 2 |
|  |  | Second | 8 | 16 | 1 | 2 |
| iii) | 3001 to 10000 | First | 13 | 13 | 0 | 2 |
|  |  | Second | 13 | 26 | 1 | 2 |
| iv) | 10001 and above | First | 20 | 20 | 0 | 3 |
|  |  | Second | 20 | 40 | 3 | 4 |

B-2.8 Internal Hydrostatic Pressure Test (Short Term - Acceptance Test)

B-2.8.1 The lot, having been found satisfactory according to B-1.4, B-1.5, B-1.6 and B-1.7 shall be subjected to the requirements of the acceptance test for internal hydrostatic pressure as given in 9.1 for test parameters as per Sl. No. (i) of Table 4. The number of fittings to be taken from the lot shall depend on the size of the lot and shall be according to Table 7.

B-2.8.2 The fittings shall be taken at random from the lot.  In order to ensure the randomness of selection, procedures given in IS 4905 may be followed.

B-2.8.3 Number of Tests and Criteria for Conformity

The number of test samples shall be as given in Table 7.  The lot shall be considered to have satisfied the requirements for this test, if the number of test samples failing in this requirement is equal to the corresponding acceptance number given in column 4 of Table 7.

### Table 7 Scale of Sampling for Internal Hydrostatic Test

(Clauses B-2.8.1 and B-2.8.3)

| Sl No. | Number of Fitting in the Lot | Sample Size | Acceptance Number |
| --- | --- | --- | --- |
| (1) | (2) | (3) | (4) |
|  | Up to 3 000 | 2 | 0 |
|  | 3 001 to 10000 | 3 | 0 |
|  | 10 001 and above | 5 | 0 |

ANNEX C

(Foreword)

COMMITTEE COMPOSITION

Plastic Piping Systems Sectional Committee, CED 50

| Organization | Representative(s) |
| --- | --- |
| Central Institute of Plastic Engineering and Technology, Chennai | Dr S. K. Nayak (Chairman) |
| Borouge India Pvt Ltd, Mumbai | Shri Prashant D. Nikhade |
| Brihan Mumbai Licensed Plumbers Association, Mumbai | Shri Kishor V. Merchant Shri Bijal M. Shah (Alternate) |
| Central Institute of Plastic Engineering and Technology, Chennai | Dr S. N. Yadav Shri D. Anjaneya Sharma (Alternate) |
| Central Public Health Environmental Engineering Organization, New Delhi | Adviser (PHE) Assistant Adviser (PHE) (Alternate) |
| Central Public Works Department, New Delhi | Shri M. K. Sharma Shri Amar Singh (Alternate) |
| Chennai Metropolitan Water Supply &Sewerage Board, Chennai | Engineering Director Superintending Engineer (P&D) (Alternate) |
| CSIR-Central Building Research Institute, Roorkee | Dr B. Singh Shri Rajiv Kumar (Alternate) |
| CSIR-National Environmental Engineering Research Institute, Nagpur | Dr (Smt) Abha Sargonkar Dr Ritesh Vijay (Alternate) |
| Delhi Development Authority, New Delhi | Superintending Engineer(D) Executive Engineer (R&D) (Alternate) |
| Delhi Jal Board, New Delhi | Shri Y. K. Sharma Shri S. L. Meena (Alternate) |
| Department of Chemical & Petrochemicals Govt. of India, New Delhi | Joint Industrial Advisor |
| Finolex Industries Limited, Pune | Shri Arun Sonawane Shri D.J. Salunke (Alternate) |
| GAIL India Limited, New Delhi | Shri Manish Khandelwal Shri Kuldeep Negi (Alternate - I) Shri Nitin Gupta (Alternate - II) |
| Government e-Marketplace, New Delhi | Representative |
| Haldia Petrochemicals Ltd, Kolkata | Shri Raj K. Datta Shri Amartya Maity (Alternate) |
| HPCL – Mittal Energy Ltd, Noida | Shri Vineet Kumar Gupta Shri Alakesh Ghosh (Alternate) |
| HSIL Ltd (Pipe Divison), Hyderabad | Shri Tushar Lokare Shri Vinoy Kumar (Alternate) |
| Indian Oil Corporation Ltd, Panipat | Shri Dhananjay Sahoo Shri Raja Poddar (Alternate) |
| Jain Irrigation System Limited, Jalgaon | Shri S. Narayanaswami Shri P. H. Chaudhari (Alternate) |
| Kolkata Municipal Corporation, Kolkata | Shri D.K. Sanyal Shri A.K. Biswas (Alternate) |
| Mahindra EPC Irrigation Ltd, Nashik | Shri Sankar Kumar Maiti Shri C.V. Joshi (Alternate) |
| Military Engineer Services, Engineer-in-Chief’s Branch,Integrated HQ of MoD(Army), New Delhi | Shri A. K. Dubey Shri R. K. Chauhan (Alternate) |
| Ministry of Drinking Water and Sanitation, New Delhi | Shri Dinesh Chand Shri Sumit Priyadarshi (Alternate) |
| NSF Safety and Certification India PvtLtd, Gurugram | Shri B. B. Singh Shri Nasrin Kashefi (Alternate) |
| Odisha PVC Pipes Manufacturing Association, Bhubaneswar | Shri Nikunj Chhotray |
| Panchayati Raj and Drinking WaterDepartment, Govt. of Odisha,Bhubaneswar | Chief Engineer |
| Plastindia Foundation, Mumbai | Shri Rajiv J. Raval Dr E. Sundaresan (Alternate) |
| Public Health Engineering Department, Jaipur | Superintending Engineer Executive Engineer (Alternate) |
| Reliance Industries Limited, Mumbai | Shri S. V. Raju Shri Saurabh Baghal (Alternate) |
| RITES Limited, New Delhi | Shri Pankaj Aggarwal Shri Mukesh Sinha (Alternate) |
| Shaktiman Extrusions Pvt Ltd, Perumbavoor | Shri N.Suresh Shri T.S. Manoj (Alternate) |
| Supreme Industries Limited, Jalgaon | Shri G. K. Saxena |
| Tamil Nadu Water Supply & Drainage Board, Chennai | Engineering Director Joint Chief Engineer (COM) (Alternate) |
| Tata Consulting Engineers Ltd, Mumbai | Representative |
| In Personal Capacity (A-59, Sector 35, Noida 201301) | Shri Kanwar A. Singh |
| In Personal Capacity (L-202 Metrozone, Anna Nagar West Chennai 600040) | Shri G.K. Srinivasan |
| BIS Directorate General | Shri Sanjay pant, Scientist ‘F’ And Head (CED) [Representing Director General (Ex-officio)] |
| Member Secretary Shrimati Madhurima Madhav Scientist ‘D’ (Civil Engg), BIS |  |