**IS 15450:\*\*\*\*\*\***

**Doc : CED 50 (13686)**

*भारतीय मानक*

**तप्त और अतप्त जल आपूर्ति के लिए पॅालीइथाईलिन-एल्युमिनियम-पॅालीइथाईलिन सम्मिश्र के दाब पाईप – विशिष्टि**

(*पहला* *पुनरीक्षण*)

*Indian Standard*

**POLYETHYLENE-ALUMINIUM-POLYETHYLENE**

**COMPOSITE PRESSURE PIPES FOR HOT AND COLD**

**WATER SUPPLIES — SPECIFICATION**

 (*first revision*)

**ICS 83.140.30, 91.140.60**

© BIS 2020

**B U R E A U O F I N D I A N S T A N D A R D S**

MANAK BHAVAN, 9 BAHADUR SHAH ZAFAR MARG

NEW DELHI 110002

*March* 2020 **Price Group**

Plastic Piping Systems Sectional Committee, CED 50

**FOREWORD**

This Indian Standard (*first revision*) was adopted by the Bureau of Indian Standards, after the draft finalized by the Plastic Piping Systems Sectional Committee had been approved by the Civil Engineering Division Council.

This standard has been published to cover requirements for polyethylene-aluminium-polyethylene (PE-AL-PE) composite pressure pipes for hot and cold water supplies.

The multilayer PE-AL-PE composite pipe comprises one metallic layer, tie layers of polymeric adhesive and inner and outer layers of polyethylene. The inner and outer layers are bonded to metallic layer which is welded aluminium tube, by polymeric adhesive during extrusion process.

This standard relates only to metal and plastic composite pipes incorporating a welded metallic tube. The welded metallic tube itself is capable of sustaining internal pressures. The pipes consisting of metallic layers not welded together are outside the scope of this standard. This standard excludes cross-linked polyethylene-aluminium-cross-linked polyethylene (PEX-AL-PEX) pipes.

This standard was first published in 2004. This revision of the standard has been taken up to update it to take into account technological advancements and experience gained in the manufacturing and use of this product.

The following major modifications have been incorporated in this revision of the standard:

1. The pipe designation has been defined based on the outside diameter (OD) as against nominal inside and outside diameter followed earlier, as per standard practice followed in other Indian Standards for plastic pipes.
2. Nominal pipe sizes, 63 mm (OD) and 75 mm (OD) which are being used in the country have been added.
3. Requirement of PE material to be used for manufacture of pipes has been modified.
4. Grade of aluminium strips has been specified.
5. Aluminium strip thickness as well as total wall thicknesses have been revised.
6. Requirement of UV stabilizer has been modified to clearly define the requirement for black pipes and coloured (other than black) pipes.
7. Layer separation test has been included for pipe sizes 40 mm OD and above.
8. The guideline for outside storage has been updated and guidelines for supply, handling, transportation and storage of PE-AL-PE composite pipes has been added.
9. Requirements of connectors and fittings for use with polyethylene/aluminium/polyethylene composite pressure pipes have been updated and additional tests have been included.

The requirements and test methods covered in this standard are to be carried out on PE-AL-PE composite pipes. Tests on the individual layers that comprise this composite pipe are outside the scope of this standard.

The standard also provides guidelines for storage, handling, installation including connectors and fittings required for use with PE-AL-PE composite pressure pipes.

This standard does not purport to address all the safety problems associated with the use. It is the responsibility of the users of this standard to establish appropriate safety and health practices and determine the applicability or regulatory safety and health practices and determines the applicability of regulatory limitation prior to use.

In the formulation of this standard considerable assistance has been derived from ASTM F 1282- 2017: ‘Standard Specification for Polyethylene/Aluminum/Polyethylene (PE-AL-PE) Composite Pressure Pipe’.

The composition of the technical committee responsible for formulation of this standard is given in Annex G.

For the purpose of deciding whether a particular requirement of this standard is complied with, the final value, observed or calculated, expressing the result of test or analysis, shall be rounded off in accordance with IS 2:1960 ‘Rules for rounding off numerical values *(revised)’.* The number of significant places retained in the rounded off value should be the same as that of the specified value in this standard.

**IS 15450:\*\*\*\***

***Indian Standard***

**POLYETHYLENE-ALUMINIUM-POLYETHYLENE**

**COMPOSITE PRESSURE PIPES FOR HOT AND COLD**

**WATER SUPPLIES — SPECIFICATION**

(*First Revision*)

1. **SCOPE**
2. This standard covers coextruded polyethylene composite pressure pipes with an aluminium welded tube reinforced between the inner and outer layers of polyethylene (PE). The inner and outer polyethylene layers are bonded to the aluminium tube by melt adhesive. The nominal pipes sizes, 12 mm to 75mm outside diameter are covered in this standard. These pipes are used for conveyance of hot and cold water supply for domestic and industrial purposes, municipal water services including internal and external plumbing, air conditioning and heating installations within buildings, underground irrigation systems, gases and chemicals that are compatible with pipe.
3. This standard relates only to metal and plastic composite pipes incorporating a welded metallic tube. The welded metallic tube itself is capable of sustaining internal pressures. The pipes consisting of metallic layers not welded together are outside the scope of this standard.
4. This standard excludes cross-linked polyethylene-aluminium-cross-linked polyethylene (PEX-AL-PEX) pipes.
5. **REFERENCES**

The standards listed below contain provisions which through reference in this text, constitute provision of this standard. At the time of publication, the editions indicated were valid. All standards are subject to revision and parties to agreements based on this standard are encouraged to investigate the possibility of applying the most recent editions of the standards indicated below:

|  |  |
| --- | --- |
| *IS No.* | *Title* |
| 737:2008 | Wrought aluminium and aluminium alloy sheet and strip for general engineering purposes — Specification (*fourth revision)* |
| 2530:1963  | Methods of test for polyethylene moulding materials and polyethylene compounds |
| 4905:2015 | Random sampling and randomization procedures (*first revision*) |
| 4984:2016 | Polyethylene pipes for water supply — Specification (*fifth revision*) |
| 7328:1992 | High density polyethylene materials for moulding and extrusion (*first revision*) |
| 9845:1998 | Determination of overall migration of constituents of plastics materials and articles intended to come in contact with foodstuffs — Method of analysis (*second revision*) |
| 10146:1982 | Specification for polyethylene for its safe use in contact with foodstuff, pharmaceuticals and drinking water |
| 14885:2001 | Polyethylene pipes for supply of gaseous fuels- Specification |
| 16738:2018 | Positive list of constituents for polypropylene, polyethylene and their copolymers for its safe use in contact with food stuffs and pharmaceuticals |

1. **TERMINOLOGY**

For the purpose of this standard, terms and definitions given in IS 4984 shall apply.

1. **PIPE DESIGNATION**

PE-AL-PE composite pipes are designated by nominal outside diameters.

NOTE — The concept of dimension ratio is not relevant to PE-AL-PE pipe and are not used to relate pressure rating with total wall thickness.

1. **MATERIALS**
	1. The material from which PE-AL-PE pipe is manufactured shall comprise of polyethylene plastic and aluminium strip.
	2. **Polyethylene**

**5.2.1** The grade of polyethylene material used for manufacture of these pipe sshall be PE 80 as defined in Table 1 of IS 4984.

The raw material characteristics like melt flow rate, base density, thermal stability and anti-oxidant content of polyethylene material used for the manufacture of these pipes shall conform to the material characteristics as mentioned in Table 3. In addition, the resin shall conform to the requirements of **3.4** of IS 10146 and to those of **5.6.2** of IS 7328.

The material grade classification and conformity to Table 3,**3.4** of IS 10146 and **5.6.2** of IS 7328 shall be provided by the raw material (resin) manufacture with documentation duly certified by resin manufacturer.

**5.2.1.1**The other constituents used should be from the positive list of constituents of PE in contact with foodstuff and pharmaceuticals as per IS 16738 and should not constitute a toxic hazard, shall not support microbial growth and shall not give rise to an unpleasant taste or odour, cloudiness or discolouration of the water.

* 1. **UV Stabilizer**

Outer PE layer of black coloured pipes shall be added with carbon black to a proportion of 2.5±0.5 percent for UV resistance.

Outer PE layer of coloured pipes shall be suitably UV stabilized. The percentage of UV stabilizer shall not be more than 0.5 percent by mass of finished compound. Raw material/master batch supplier shall provide a certificate specifying the active content of UV stabilizer in their supply.

NOTE — In case of coloured pipes (other than black), the manufacturer shall also declare the maximum permitted exposure time in sun.

* 1. **Aluminium**

The material shall conform to Grade 31200 of IS 737 and shall have the following properties when tested as per IS 737,

1. Minimum elongation : 20 percent
2. Ultimate tensile strength : 95MPa, *Min*

The aluminium strip shall have minimum thickness and tolerance thereon as specified in Table 1.

## **Table 1 Aluminium Thickness and Tolerances for PE-AL-PE Pipe**

(*Clause* 5.4)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Nominal Pipe size (OD)**mm | **Minimum Aluminium Thickness**mm | **Tolerance on minimum Aluminium Thickness**mm |
| (1) | (2) | (3) | (4) |
|  | 12 | 0.18 | +0.03 |
|  | 14 | 0.18 | +0.03 |
|  | 16 | 0.18 | +0.03 |
|  | 20 | 0.23 | +0.03 |
|  | 25 | 0.23 | +0.03 |
|  | 32 | 0.28 | +0.03 |
|  | 40 | 0.33 | +0.03 |
|  | 50 | 0.47 | +0.04 |
|  | 63 | 0.57 | +0.04 |
|  | 75 | 0.67 | +0.05 |

* 1. **Rework Material**

No rework material shall be used in the manufacture of pipe.

1. **PRESSURE RATING**

The PE-AL-PE composite pipe meeting the requirements of this standard shall be pressure rated for maximum water pressures of 1.38 MPa at 23°C, 1.10 MPa at 60°C and 0.69 MPa at 82°C.

**7 NOMINAL DIAMETERS**

The nominal outside diameter of pipes covered are 12, 14, 16, 20,25,32,40, 50, 63 and 75 mm. Respective nominal inside diameters for the above pipe sizes are 9, 10, 12, 16, 20, 25, 32, 40, 50 and 63mm, respectively.

**8 COLOUR**

The colour of the outer layer of the pipe shall be black or any other colour as per the requirement of the customer. In case of coloured pipes (other than black), the manufacturer shall also declare the maximum permitted exposure time in sun.

**9 DIMENSIONS OF PIPE**

**9.1** Pipe outside diameter, tolerance on outside diameter, out-of-roundness, wall thickness and minimum thickness of outer layer of polyethylene shall be as given in Table 2. The minimum thickness of the outer polyethylene material overlaying the weld, shall be half of that specified in Table 2.The thickness of aluminium layer shall be as given in Table 1.

* 1. **Method of Measurements**

**9.2.1**The outside diameter of pipe shall be taken as the average of two measurements taken at right angles. The wall thickness shall be measured by a dial vernier or ball ended micrometer. The resulting dimension shall be expressed to the nearest 0.1 mm.

**9.2.2**Ovality shall be measured as the difference between maximum outside diameter and minimum outside diameter measured at the same cross section of the pipe. For pipes to be coiled, the ovality shall be measured prior to coiling. For coiled pipes, however, re-rounding of pipes shall be carried out prior to the measurement of ovality.

**9.2.3**The thickness of the outer layer of polyethylene in the PE-AL-PE pipe shall be tested in accordance with Annex B.

## **Table 2 Overall Pipe Dimensions**

(*Clause* 9.1)

All dimensions in millimetres.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Sl. No.** | **Nominal Pipe Size** | **Pipe Outside Diameter (OD)** | **Tolerance on Outside Diameter**  | **Maximum Out of Roundness**  | **Total Wall Thickness** | **Outer PE layer Thickness***Min* |
| Minimum | Maximum |
|  (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |
| i) | 12 | 12.00 | $$\begin{matrix}+0.30\\-0.00\end{matrix}$$ | 0.30 | 1.60 | 2.00 | 0.40 |
| ii) | 14 | 14.00 | $$\begin{matrix}+0.30\\-0.00\end{matrix}$$ | 0.40 | 1.60 | 2.00 | 0.40 |
| iii) | 16 | 16.00 | $$\begin{matrix}+0.30\\-0.00\end{matrix}$$ | 0.40 | 1.70 | 2.10 | 0.40 |
| iv) | 20 | 20.00 | $$\begin{matrix}+0.30\\-0.00\end{matrix}$$ | 0.60 | 1.90 | 2.30 | 0.40 |
| v) | 25 | 25.00 | $$\begin{matrix}+0.30\\-0.00\end{matrix}$$ | 0.60 | 2.30 | 2.80 | 0.40 |
| vi) | 32 | 32.00 | $$\begin{matrix}+0.50\\-0.00\end{matrix}$$ | 0.80 | 2.90 | 3.50 | 0.40 |
| vii) | 40 | 40.00 | $$\begin{matrix}+0.50\\-0.00\end{matrix}$$ | 1.00 | 3.90 | 4.50 | 0.40 |
| viii) | 50 | 50.00 | $$\begin{matrix}+0.50\\-0.00\end{matrix}$$ | 1.30 | 4.40 | 5.00 | 0.40 |
| ix) | 63 | 63.00 | $$\begin{matrix}+0.60\\-0.00\end{matrix}$$ | 1.40 | 5.80 | 6.40 | 0.40 |
| x) | 75 | 75.00 | $$\begin{matrix}+0.60\\-0.00\end{matrix}$$ | 1.50 | 7.30 | 7.90 | 0.40 |

**9.3 Length of Straight Pipe**

The pipe shall be supplied in straight lengths between 3 and 20 m, as per the requirement of the purchaser.

**9.4 Coiling**

While coiling, the inside diameter of coils shall not be less than 20 times the outside diameter of pipe.

**10VISUAL APPEARANCE**

The internal and external surfaces of the pipe shall be smooth, clean and free from grooving and other defects. The ends shall be cleanly cut and shall be square with the axis of the pipes. Slight shallow longitudinal grooves or irregularities in the wall thickness shall be permissible provided that the wall thickness remains within the permissible limits.

**11PERFORMANCE REQUIREMENTS**

**11.1Density**

When tested as per IS 7328 on a composite sample of PE materials from layers of minimum 3pipes, the base density shall meet the requirement as given in Table 3.

NOTE — The test is to be carried out on the polyethylene layers of the pipe.

**11.2Melt Flow Rate**

When tested as per IS 2530 at 190°C with nominal load of 5 kgf, on a combined sample of PE material generated from layers of minimum3 pipes, the MFR of the pipe shall meet the requirement in Table 3, and shall not deviate by more than 30percent of the MFR of the material used in manufacturing of pipes.

NOTE — The test is to be carried out on the polyethylene layers of the pipe.

**11.3 Overall Migration**

When tested as per IS 9845 on samples of 3 pipes, the overall migration of constituents shall be within the limits stipulated in IS 10146.

**11.4 Thermal Stability to Oxidation**

The minimum oxidation induction time (OIT) of the PE material from the pipe when tested in accordance with the method given in Annex B of IS 4984 (*see* Table 3) shall not be less than 20 min at 200⁰C.

NOTE — The test is to be carried out on the polyethylene layers of the pipe.

**11.5Carbon Black Content and Dispersion**

When tested as per IS 2530 on a composite sample of black PE material generated from outer layers of minimum 3pipes, it shall meet the carbon black content requirement as given in Table 3. When tested as per Annex B of IS 7328, on a composite sample of black PE material from outer layers of minimum 3 pipes, the dispersion of carbon black shall be satisfactory.

NOTE — The test is to be carried out on the polyethylene layers of the pipe.

**11.6Pigment Dispersion (For Coloured Pipes)**

When tested as per Annex A of IS 14885 on a composite sample of coloured PE material (other than black) generated from outer layers of minimum 3 pipes, the grading shall be ≤ 3.

**11.7 Resistance to Weathering**

After exposure to sunlight in accordance with Annex B of IS 14885, coloured PE pipes (other than black) shall comply with the requirements given in **5.6** of IS 14885.

NOTE — The tests are to be carried out on the outer polyethylene layer of the pipe.

**Table 3 PE Compound Characteristics**

(*Clauses* 11.1, 11.2, 11.4, 11.5, 11.6)

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **SI****No.** | **Characteristics** | **Unit** | **Requirement** | **Test****Parameter** | **Method of Test, Ref to** |
|  |  |  |  |  | IS No. | Annex |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) |
| i) | Base Density | kg/m3 | 940.4 to 946.4 | 27°C | IS 7328 |  |
|  |  |  | 942.0 to 948.0 | 23°C | IS 7328 | - |
| ii)  | Melt flow rate | g/10 min | 0.4 to 0.8Maximum deviation of ± 30 percent of the nominated value declared by the compound producer | 190°C/5kg | IS 2530 | - |
| iii) | Carbon black content | By mass | 2.5±0.5 percent | - | IS 2530 | - |
| iv) | Carbon black dispersion (black pipes) | Grade | ≤ 3 |  |  | Annex B of IS 7328 |
| v) | Pigment dispersion (coloured pipes other than black) | Grade | ≤ 3 |  | - | Annex A of IS 14885 |
| vi) | Thermal stability (oxidation induction time) | min | ≥ 20 | 200 °C | - | Annex B of IS 4984 |
| vii) | Anti-oxidant | By mass | ≤ 0.3 percent | - | IS 2530 | - |

**11.7 Adhesion Test**

**11.7.1** *De-lamination Test* (*Pipe Size 12mm to 32mm*)

When tested in accordance with C-1, there shall be no delamination of the PE and AL, either on bore side or the outside.

**11.7.2** *Layer Separation Test* (*Pipe Size 40 mm and Above*)

When tested in accordance with C-2, minimum adhesive force per 10mm length of pipe strip shall be as specified in Table 4.

**Table 4Minimum Adhesive Force**

(*Clause* 11.7.2)

|  |  |  |
| --- | --- | --- |
| **Sl. No.** | **Nominal Pipe Size**mm | **Minimum Adhesive Force per 10 mm Pipe Section** N |
| (1) | (2) | (3) |
|  | 40 | 40 |
|  | 50 | 50 |
|  | 63 | 60 |
|  | 75 | 70 |

**11.8Apparent Tensile Strength of Pipe**

The pipe rings when tested in accordance with Annex D shall meet the minimum requirement as specified in Table 5.

**11.9Minimum Burst Pressure**

The minimum burst pressure for PE-AL-PE pipe shall be as given in Table 5, when determined in accordance with Annex E.

###### **Table 5Minimum Pipe Ring Strengths at 23°C**

###### **Burst Pressure of PE-AL-PE Pipe**

(*Clauses* 11.8 and 11.9)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl****No.** | **Nominal Pipe Size**(mm) | **Minimum Pipe Ring Strength**(N) | **Minimum Burst Pressure**(MPa) |
| (1) | (2) | (3) | (4) |
| i) | 12 | 2000 | 7.0 |
| ii) | 14 | 2000 | 7.0 |
| iii) | 16 | 2100 | 6.0 |
| iv) | 20 | 2400 | 5.0 |
| v) | 25 | 2400 | 4.0 |
| vi) | 32 | 2650 | 4.0 |
| vii) | 40 | 3200 | 4.0 |
| viii) | 50 | 3500 | 3.8 |
| ix) | 63 | 5200 | 3.8 |
| x) | 75 | 6000 | 3.8 |

**11.10 Hydraulic Characteristics**

**11.10.1** *Short Term Hydrostatic Tests*

When subjected to internal pressure creep rupture test in accordance with procedure given in Annex F, the pipe under test shall show no sign of localized swelling, leakage or weeping, and shall not burst during the prescribed test duration. The temperatures, duration of test and pressure for the test shall conform to those specified in Table 6.

# **Table 6 Hydraulic Pressure Test Conditions and**

# **Requirements for PE-AL-PE Pipe**

(*Clause* 11.10.1)

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Sl. No.** | **Nominal Pipe Size** mm | **Test Temperature**$°$C | **Test Pressure**MPa | **Minimum Test duration** h |
|  |  |  |  |  |
| (1) | (2) | (3) | (4) | (5) |
| i) | 12 | 2760 | 3.22.5 | 110 |
| ii) | 14 | 2760 | 3.02.5 | 110 |
| iii) | 16 | 2760 | 3.02.5 | 110 |
| iv) | 20 | 2760 | 2.72.5 | 110 |
| v) | 25 | 2760 | 2.62.5 | 110 |
| vi) | 32 | 2760 | 2.62.5 | 110 |
| vii) | 40 | 2760 | 2.62.1 | 110 |
| viii) | 50 | 2760 | 2.42.1 | 110 |
| ix) | 63 | 2760 | 2.42.1 | 110 |
| x) | 75 | 2760 | 2.42.1 | 110 |

**11.10.2** *Long Term Hydrostatic Test*

When subjected to internal pressure creep rupture test in accordance with procedure given in Annex F, the pipe under test shall show no sign of localized swelling, leakage or weeping, and shall not burst during the prescribed test duration. The temperatures, duration of test and pressure for the test shall conform to those specified in Table 7.

## **Table 7 Long Term Hydrostatic Test**

(*Clause* 11.10.2)

| **Sl No.** | **Nominal Pipe Size** mm | **Test Temperature**°C | **Test Pressure** MPa | **Minimum test duration**h |
| --- | --- | --- | --- | --- |
| (1)  | (2) | (3) | (4) | (5) |
| i) | 12 | 95 | 1.3 | 170 |
| ii) | 14 | 95 | 1.3 | 170 |
| iii) | 16 | 95 | 1.2 | 170 |
| iv) | 20 | 95 | 1.0 | 170 |
| v) | 25 | 95 | 1.0 | 170 |
| vi) | 32 | 95 | 0.9 | 170 |
| vii) | 40 | 95 | 0.9 | 170 |
| viii) | 50 | 95 | 0.9 | 170 |
| ix) | 63 | 95 | 0.9 | 170 |
| x) | 75 | 95 | 0.9 | 170 |

**12SAMPLING, FREQUENCY OF TESTS AND CRITERIA FOR CONFORMITY**

**12.1 Type Test**

Type tests are intended to prove the suitability and performance of a new composition, a new manufacturing technique or a new size of pipe. Such tests need to be carried out only when a change is made in the polymer composition or method of manufacture, or when a new size is to be introduced. Even if no change is envisaged, type test shall be done at least once in three years on the highest size (lowest size for overall migration test) manufactured during the period.

Type tests shall include the following:

1. Long term hydrostatic test;
2. Overall migration test;
3. Resistance to weathering; and
4. Thermal stability to oxidation.

**12.1.1** *Long Term Hydrostatic Test*

Three samples of same size selected at random from the regular production lot shall be tested for compliance with the requirement of the type test as per **11.10.2** and Table 7.

**12.1.2** *Overall Migration Test*

Three samples of the smallest size of the pipe manufactured from each of the machines shall be selected at random from the regular production lot and tested for compliance as per **11.3**.

**12.1.3** *Thermal Stability to Oxidation*

Three samples of same size selected at random from the regular production lot shall be tested for compliance with the requirement of the type test as per **11.4**.

**12.1.4** If all the samples pass the requirements of the type test, the size of the pipe under consideration shall be considered eligible for the type approval.

**12.1.5** In case any of the samples fails in the type test, the testing authority, at its discretion, may call for fresh samples not exceeding the original number and subject them to the type test again. If in repeat test, no single failure occurs, the size of the pipe under consideration shall be considered eligible for the type approval. If any of the samples fails in the repeat tests, the size of the pipe under consideration shall not be approved. The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

**12.1.6** At the end of validity period (normally 3 years) or earlier as may be necessary, the testing authority may call for fresh samples for type test for the purpose of type approval.

**12.2Acceptance Test**

**12.2.1** Acceptance tests are carried out on samples selected from a lot for the purpose of acceptance of the lot.

**12.2.2***Lot*

All pipes of the same size and manufactured essentially under similar conditions of manufacture shall constitute a lot. For ascertaining the conformity of the lot to the requirement of this specification, samples shall be selected in accordance with the provision as mentioned under **12.2.3** and **12.2.4** and tested for compliance.

**12.2.3***Dimensional and Visual Requirements*

**12.2.3.1**The number of test samples shall be in accordance with Table 8.

**12.2.3.2**These pipes shall be selected at random from the lot and in order to ensure the randomness of selection a random number table shall be used. For guidance and use of random number table, IS 4905 may be referred. In absence of a random number table the following procedure may be adopted:

Starting from any pipe in the lot, count them as 1,2,3, 4, etc, up to $r$and so on where $r$is the integral part of $N/n$*,* $N$being the number of pipes in the lot and $n $is the number of pipes in the samples. Every $r$th pipe so counted shall be drawn so as to constitute the required sample size.

##### **Table 8 Scale of Sampling for Visual and Dimensional Requirements**

(*Clauses* 11.2.3.1 *and* 11.2.3.3)

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **SI No.** | **No. of Pipes/Coils in the Lot** | **Sample No.** | **Sample Size** | **Cumulative Sample Size** | **Acceptance No.** | **Rejection****No.** |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) |
| i) | Up to 25 | First | 3 | 3 | 0 | 2 |
|  |  | Second | 3 | 6 | 1 | 2 |
| ii) | 26 to 150 | First | 13 | 13 | 0 | 2 |
|  |  | Second | 13 | 26 | 1 | 2 |
| iii) | 151 to 280 | First | 20 | 20 | 0 | 3 |
|  |  | Second | 20 | 40 | 3 | 4 |
| iv) | 281 to 500 | First | 32 | 32 | 1 | 4 |
|  |  | Second | 32 | 64 | 4 | 5 |
| v) | 501 to 1 200 | First | 50 | 50 | 2 | 5 |
|  |  | Second | 50 | 100 | 6 | 7 |
| NOTE — Pipes are usually manufactured in coils only. Pipes in straight lengths are seldom manufactured. Same sampling will be applicable for pipes manufactured in straight length. |

**12.2.3.3**The number of pipes given for the first sample in col 3 of Table 8 shall be examined for dimensional and visual requirements given in **9.1**,**9.2**, **9.3** and **10**. A pipe failing to satisfy any of these requirements shall be considered as defective. The lot shall be deemed to have satisfied these requirements, if the number of defectives found in the first sample are less than or equal to the corresponding acceptance number given in col 6 of Table 8. The lot shall be deemed not to have met these requirements, if the number of defectives found in the first sample is greater than or equal to the corresponding rejection number given in col 7 of Table 8. If however, the number of defectives found in the first sample lies between the corresponding acceptance and rejection numbers given in col 6 and col 7 of Table 8, second sample of size given in col 4 of Table 8 shall be taken and examined for these requirements. The lot shall be considered to have satisfied these requirements if the number of defectives found in the cumulative samples is less than or equal to the corresponding acceptance number given in col 6 of Table 8; otherwise not.

**12.2.4** The lot having satisfied dimensional and visual requirements shall be tested for hydraulic characteristics, density, MFR, carbon black content and dispersion, adhesion, apparent tensile strength, minimum burst pressure and pigment dispersion (for coloured pipes other than black) tests requirements.

**12.2.4.1**A separate sample size for each of the tests shall be taken as stipulated in Table 9 and selected at random from the sample already examined for dimensional and visual inspection. All the pipes in each of the sample size shall be tested for compliance in the requirement for density (*see* **10.1**),MFR (*see* **10.2**), carbon black content and dispersion (*see* **10.3**), pigment dispersion (*see* **10.4**)**,** adhesion (*see* **10.5**), apparent tensile strength (*see* **10.6**), minimum burst pressure (*see* **10.7**) and hydraulic characteristics (*see* **10.8**). The lot shall be considered to have met the requirements of these tests, if none of the sample tested fails.

**Table 9 Scale of Sampling for Tests for Hydraulic Characteristics, Density, MFR, Carbon Black Content and Dispersion, Adhesion, Apparent Tensile Strength, Minimum Burst Pressure and Pigment Dispersion**

(*Clause* 12.2.4.1)

|  |  |  |
| --- | --- | --- |
| **SI No.** | **No. of Pipes/Coils** | **Sample Size** |
| (1) | (2) | (3) |
| i) | Up to 100 | 3 |
| ii) | 101 to 150 | 4 |
| iii) | 151 to 200 | 5 |
| iv) | 201 and above | 8 |

#### 13MARKING

**13.1**The marking shall be repeated at intervals of 1mand shall consist the following information:

1. Manufacturer’s name or trade-mark;
2. Pipe designation; and
3. Lot number/Batch number containing information of date of manufacture.

**13.1.1** The lot number/batch number shall include the details of production in the following manner:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Year | Month | Day | Machine No. | Shift |  |
|  xxxx |  xx | xx |  xxx | x |  |

**13.2**Two labels of suitable dimensions should be carefully attached to each coil indicating:

1. Supplier’s name;
2. Manufacturing standard;
3. Pipe designation;
4. Weight of coil, in kg; and
5. Length of coil, in m.

**13.3 BIS Certification Marking**

Each pipe conforming to the requirements of this standard may be certified as per the conformity assessment schemes under the provisions of the *Bureau of Indian Standards Act, 2016* and the Rules and Regulations framed thereunder, and the pipe may be marked with the Standard Mark.

**ANNEX A**

(*Foreword* and *Clause* 1.4)

**RECOMMENDATORY INFORMATION**

**A-1 SUPPLY, HANDLING, TRANSPORTATION ANDSTORAGE**

**A-1.1 Supply**

The PE-AL-PE composite pipes shall be supplied as self-supporting coils, straight length either independent or bundled together, or as agreed between supplier and purchaser. Their ends shall be cleanly cut, square with the axis of pipe and protected against shocks and ingress of foreign bodies by appropriate end caps.

**A-1.1.1** *Coils*

PE-AL-PE composite pipes shall be coiled and coils should be stored flat or vertically in purpose-built racks or cradles, if desired by purchaser. Consideration should be given for facilities, which avoid single point contact of the coils.

**A-1.1.1.1**All coiled pipe shall be constrained in a stable configuration by banding with PP/HDPE strap at least three equi-spaced positions during production. The banding shall be sufficiently stable to prevent movement.

**A-1.1.1.2** Coiled pipe shall preferably be packed in woven fabric bags or wrapped with woven fabrics. The woven fabric shall be HDPE or PP.

**A-1.1.2** *Bundles*

The distance (X) between the supporting frames shall be equally spaced in order to allow stacking (*see* Fig. 1).The PE-AL-PE composite straight length pipe shall rest evenly over their whole length. The supporting frame must not be nailed together and must be constructed such as to lead the pressure load directly through the supporting frame and not through the multilayer pipes.

The pipe bundles may be packed in woven fabric layflat tube. The woven fabric shall be HDPE or PP.

****

Fig. 1 Stacking Arrangement of Straight Length Pipes

**A-1.2 Handling**

**A-1.21** *General*

Do not drag or throw the pipes along the ground. If handling equipment is not used, choose techniques which are not likely to damage the pipe.

**A-1.2.2***Coils*

Individual coils must not be rolled off the edge of the loading platforms or trailers. These coils may be kept on pallets and loaded, off-loaded using forklifts, pallet trolley, etc.

**A-1.2.3***Straight Pipe*

Initial handling and storage of composite straight pipes should be made with the pipe in packaged form, thus minimizing damage during this phase. When loading, unloading or handling, it is preferable to use mechanical equipment to move or stack the packs.

**A-1.3 Transportation**

**A-1.3.1** *Coiled Pipe*

Coiled pipe may be supplied on pallets. The coils should be firmly strapped to the pallets, which should in turn be firmly secured to the vehicle. There should be facilities to restrain each coil securely throughout transit and the loading process.

To save on transport cost nesting of coils/straight length can be considered if agreed between the purchaser and the supplier.

**A-1.3.2***Straight Lengths*

When transporting straight PE-AL-PE composite pipes, use flatbed vehicles with a partition. The bed shall be free from nails and other protuberances. The pipes or pipe bundles shall rest uniformly in the vehicle over their whole length. The vehicles shall have side supports appropriately spaced 2 m apart, and the multilayer pipes shall be secured effectively during transportation. All posts shall be flat with no sharp edges. During transportation, the multilayer pipes should be continuously supported such as to minimize movement between the pipes and their supports. Also being relatively soft outer layer, poor handling techniques may result in scratches, cuts or puncture.

**A-1.4 Storage**

The composite pipes, other than black coloured pipe, shall not be stored outside, open to the sun for more than 2 years. Where individual pipe lengths and coils are stacked in pyramidal fashion, deformation may occur in the lower layers, particularly in warm weather. Therefore, such stacks should not exceed a height of 1500 mm.

The composite pipes shall be stacked on a reasonably flat surface, free from sharp objects, stones or projections likely to deform or damage them.

###### **A-2 CONNECTORS AND FITTINGS**

**A-2.1 General**

**A-2.1.1** Connectors or fittings shall be made from brass or any other material found to be suitable for the service conditions.

**A-2.1.2** The connectors or fittings shall be so designed that a seal is effected on the internal wall surface of the pipe so that the medium contained in the pipe is barred from coming in contact with the cross section of the pipe.

**A-2.1.3**PE-AL-PE pipes manufactured according to this standard shall be capable of being jointed with the connectors or fittings provided that the connector or fitting alone or in assembly with PE-AL-PE pipe complies with the requirements as given in **A-2.2**, **A-2.3** and **A-2.4**.

**A-2.2Hydrostatic Burst Pressure**

The connector or fitting assembled with PE-AL-PE pipe, shall meet the minimum hydrostatic burst pressure requirement at 60±2 °C as given in Table 10.

**Table 10 Minimum Hydrostatic Burst Pressure at 60**°**C**

(*Clause* A-2.2)

| **Sl No.** | **Pipe Size**  | **Test Pressure** MPa |
| --- | --- | --- |
| (1) | (2) | (3) |
| i) | 12 | 4.0 |
| ii) | 14 | 4.0 |
| iii) | 16 | 4.0 |
| iv) | 20 | 3.8 |
| v) | 25 | 3.2 |
| vi) | 32 | 3.2 |
| vii) | 40 | 2.5 |
| viii) | 50 | 2.3 |
| ix) | 63 | 2.0 |
| x) | 75 | 2.0 |

**A-2.3Internal Pressure Test**

The fitting or connector, when assembled with PE-AL-PE pipe, shall not fail or weep at the test pressure and ambient temperatures for the specified duration as given in Table 11. The joint shall not have any leakage during the test.

**Table 11 Test Pressure and Duration for Internal Pressure Test**

(*Clause* A-2.3)

| **Sl No.** | **Pipe Size**  | **Test Pressure**Bar | **Duration**h |
| --- | --- | --- | --- |
| (1) | (2) | (3) | (4) |
| i) | 12 | 3.6 | 1 |
| ii) | 14 | 3.6 | 1 |
| iii) | 16 | 3.43 | 1 |
| iv) | 20 | 2.67 | 1 |
| v) | 25 | 2.67 | 1 |
| vi) | 32 | 2.30 | 1 |
| vii) | 40 | 2.23 | 1 |
| viii) | 50 | 2.20 | 1 |
| ix) | 63 | 2.20 | 1 |
| x) | 75 | 2.20 | 1 |

**A-2.4Pull Out Test**

**A-2.4.1***Apparatus*

The apparatus shall consist of one of the following:

1. A tensile testing machine together with grips capable of subjecting the test assembly to a constant longitudinal force; and
2. A frame with means for suspending a test piece together with stirrup at the lower end to hold sufficient weight(s) with which to apply the specified force.

**A-2.4.2***Test Assembly*

The test assembly shall comprise a straight coupling or any other fitting which can join two pipe pieces assembled in accordance with the manufacturer’s instructions with two pieces of pipe of the appropriate nominal size. Separate combinations shall be assembled for each type of pipe for which fitting is designed. Each pipe shall be at least 100 mm in length.

**A-2.4.3***Procedure*

Secure the test assembly in the apparatus and apply gradually over a period of 30 s the appropriate force at ambient temperature as given in Table 12 as applicable. Hold the specimen in constant tension for the specified duration.

**Table 12 Test Force and Duration for Pull Out Test**

(*Clause* A-2.4.3)

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl No.** | **Pipe Size** mm | **Test Force** *N* | **Duration** h |
| (1) | (2) | (3) | (4) |
| i) | 12 | 494 | 1 |
| ii) | 14 | 589 | 1 |
| iii) | 16 | 722 | 1 |
| iv) | 20 | 1021 | 1 |
| v) | 25 | 1550 | 1 |
| vi) | 32 | 2506 | 1 |
| vii) | 40 | 4180 | 1 |
| viii) | 50 | 5957 | 1 |
| ix) | 63 | 9851 | 1 |
| x) | 75 | 14674 | 1 |
| NOTE — The pull out test forces have been calculated using the following formula:$$F=1.5 π σ\_{∅ }(D^{2}- d^{2})/4$$where$F$ = applied force in N;$σ\_{∅ }$ = design circumferential stress = 6.3 MPa;$D$ = nominal outside diameter of the pipe in mm; and$d$= internal diameter of the pipe with minimum wall thickness in mm. |

**ANNEX B**

(*Clause* 9.1)

**OUTER POLYETHYLENE LAYER THICKNESS**

**B-1SAMPLE PREPARATION**

Select the sample of pipe at random. Cut the pipe with a sharp knife or other suitable cutter, ensuring that the pipe after cutting is not more than 1 percent out-of-roundness.

**B-2 THICKNESS DETERMINATION**

Use a hand held magnifying glass equipped with graduated reticule or a laboratory microscope with graduated reticule. The reticule should measure to the nearest 0.10 mm. Determine the thickness of outer coating of polyethylene at six points around the circumference. Only one of the points should be at the aluminium weld.

**ANNEX C**

(*Clause* 11.7)

**ADHESION TEST**

**C-1 DE-LAMINATION TEST**

**C-1.1Cutting of the Spiral**

Mount a sharp but razor like blade within a protective housing and angle to cut a 45 ± 5° spiral in the pipe. Choose a PE-AL-PE pipe at random and insert into the housing and rotate to form the spiral cut. The cut goes through the complete wall on one side of the pipe only. Run the spiral along the pipe for a minimum distance along the pipe axis equal to five times the outside diameter.

**C-1.2Examining for Delamination**

Hold pipe with the spiral cut firm at the uncut end and create a ribbon of pipe material by opening out the spiral cut pipe. Pliers can be used to grip the spiral cut pipe. Examine the wall of the pipe visually side-on for evidence of delamination between metal and plastic layers (*see* Fig. 2).



1. Good pipes showing no delamination.
2. Delamination between the inner PE layer and the aluminium.
3. Delamination between the outer PE layer and the aluminium.

Fig. 2 Delamination between Metal and Plastic Layers

**C-2 LAYER SEPARATION TEST**

The layer separation test shall be conducted at 27±2⁰C.

**C- 2.1 Test Apparatus**

The test apparatus for the layer separation test shall consist of a tension device with suitable pull of device (*see*Fig.3)

**C-2.2 Test Specimen**

The test specimen for the layer separation test shall consist of five sections of PE-AL-PE pipe, each approximately10mm long, cut at random intervals from one section of pipe.

**C-2.3 Test Procedure**

1. Mechanically separate, to about 5mm and on the opposite side to the welding seam, the outside PE layer, together with aluminium layer, from the inside PE layer of the test specimens using the pull off device.

NOTE—Separating the layer 5 mm allows clamping.

1. Examine the adhesion of the outside PE layer to the aluminium tube.
2. Mount the test specimen and clamp the 5mm tab in the tension testing device.
3. Remove the outside layer with linear speed of 50 mm/min
4. Record the force diagram.

**C-2.4 Test Performance Requirement**

The minimum adhesive force per 10mm pipe strip shall be as specified in Table 4 and there shall be no delamination or separation between the outside PE layer and the aluminium tube.



Fig.3 Setup for Layer Separation Test

**ANNEX D**

(*Clause* 11.8)

**APPARENT TENSILE STRENGTH TEST**

**D-1SAMPLE SIZE AND SHAPE**

Cut the rings of the PE-AL-PE pipe so that two sides are parallel and at 90 ± 2° to the pipe axis. The length of each ring will be 25 *±* 1 mm. Cut minimum of 15 samples consecutively along the axis of the pipe.

**D-2 RING TESTS**

Test the consecutively cut samples individually using a tensile testing machine. Arrange the rings so that the aluminium weld is at 90° to the tensile axis as shown in Fig. 4. The crosshead speed shall be at 50 ± 2.5 mm/min. Mount the rings of pipe on two steel rods of minimum diameter of 4 mm. Record the peak force.



Fig. 4 Schematic Presentation of the Pipe Ring Test Showing the Aluminium Weld at 90° to the Tensile Axis

**ANNEX E**

(*Clause* 11.9)

### MINIMUM BURST PRESSURE

**E-1PIPE SAMPLE**

Select a length of PE-AL-PE pipe at random and prepare 5 consecutive lengths of required length (200 mm minimum). Seal samples at the ends with appropriate fittings and test either free or fixed end.

**E-2 TEST TEMPERATURE**

The test should be carried out at ambient temperature inside the laboratory. The temperature should preferably be 25 ± 5°C.

**E-3 BURST PRESSURE**

Increase the pressure inside the pipe in such a way that the time required to reach the burst pressure is between 60 to 70 s.

**ANNEX F**

(*Clauses* 11.10*and* 12.1.1)

**HYDRAULIC PRESSURE TEST**

**F-1 SAMPLES**

Each test sample of PE-AL-PE pipe shall have a minimum length between end closures of at least ten times the average outside diameter of the pipe, but not less than 250 mm. Seal specimens at both ends with appropriate fittings and fill the sample with water.

**F-2 TEST PROCEDURES**

Test each sample individually in a temperature controlled water bath. Condition the test samples for at least 2 h in the water bath when the water bath is at the required test temperature as given in Table 6 and Table 7 and maintain the same till test duration. Maintain the pressure indicated in Table6 and Table 7 within ±0.07 MPa of the set pressures for the duration of the test.

**F-3 FAILURE**

Any continuous loss of pressure of the test sample shall constitute failure of the test.

**ANNEX G**

(*Foreword*)

**COMMITTEE COMPOSITION**

Plastic Piping Systems Sectional Committee, CED 50

| *Organization* | *Representative(s)* |
| --- | --- |
|
| Central Institute of Plastic Engineering and Technology, Chennai | Dr S. K. Nayak (***Chairman***) |
| Borouge India Pvt Ltd, Mumbai | Shri Prashant D. Nikhade |
| Brihan Mumbai Licensed Plumbers Association, Mumbai | Shri Kishor V. Merchant Shri Bijal M. Shah (*Alternate*) |
| Central Institute of Plastic Engineering and Technology, Chennai | Dr S. N. YadavShri D. Anjaneya Sharma (*Alternate*) |
| Central Public Health Environmental Engineering Organization, New Delhi | Adviser (PHE) Assistant Adviser (PHE) (*Alternate*) |
| Central Public Works Department, New Delhi | Shri M. K. Sharma Shri Amar Singh (*Alternate*) |
| Chennai Metropolitan Water Supply &Sewerage Board, Chennai | Engineering Director Superintending Engineer (P&D) (*Alternate*) |
| CSIR-Central Building Research Institute, Roorkee | Dr B. Singh Shri Rajiv Kumar (*Alternate*) |
| CSIR-National Environmental Engineering Research Institute, Nagpur | Dr (Smt) Abha SargonkarDr Ritesh Vijay (*Alternate*) |
| Delhi Development Authority, New Delhi | Superintending Engineer(D) Executive Engineer (R&D) (*Alternate*) |
| Delhi Jal Board, New Delhi | Shri Y. K. SharmaShri S. L. Meena (*Alternate*) |
| Department of Chemical & Petrochemicals Govt. of India, New Delhi | Joint Industrial Advisor |
| Finolex Industries Limited, Pune | Shri Arun SonawaneShri D.J. Salunke (*Alternate*)  |
| GAIL India Limited, New Delhi | Shri Manish KhandelwalShri Kuldeep Negi (*Alternate* - I)Shri Nitin Gupta (*Alternate* - II) |
| Government e-Marketplace, New Delhi | **Representative**  |
| Haldia Petrochemicals Ltd, Kolkata | Shri Raj K. DattaShri Amartya Maity (*Alternate*) |
| HPCL – Mittal Energy Ltd, Noida | Shri Vineet Kumar GuptaShri Alakesh Ghosh (*Alternate*) |
| HSIL Ltd (Pipe Divison), Hyderabad | Shri Tushar LokareShri Vinoy Kumar (*Alternate*)  |
| Indian Oil Corporation Ltd, Panipat | Shri Dhananjay SahooShri Raja Poddar (*Alternate*) |
| Jain Irrigation System Limited, Jalgaon | Shri S. NarayanaswamiShri P. H. Chaudhari (*Alternate*) |
| Kolkata Municipal Corporation, Kolkata | Shri D.K. SanyalShri A.K. Biswas (*Alternate*) |
| Mahindra EPC Irrigation Ltd, Nashik | Shri Sankar Kumar MaitiShri C.V. Joshi (*Alternate*) |
| Military Engineer Services, Engineer-in-Chief’s Branch,Integrated HQ of MoD(Army), New Delhi | Shri A. K. DubeyShri R. K. Chauhan (*Alternate*) |
| Ministry of Drinking Water and Sanitation, New Delhi | Shri Dinesh Chand Shri Sumit Priyadarshi (*Alternate*) |
| NSF Safety and Certification India PvtLtd, Gurugram | Shri B. B. SinghShri Nasrin Kashefi (*Alternate*) |
| Odisha PVC Pipes ManufacturingAssociation, Bhubaneswar | Shri Nikunj Chhotray |
| Panchayati Raj and Drinking WaterDepartment, Govt. of Odisha,Bhubaneswar | Chief Engineer  |
| Plastindia Foundation, Mumbai | Shri Rajiv J. RavalDr E. Sundaresan (*Alternate*) |
| Public Health Engineering Department, Jaipur | Superintending Engineer Executive Engineer (*Alternate*) |
| Reliance Industries Limited, Mumbai | Shri S. V. RajuShri Saurabh Baghal (*Alternate*) |
| RITES Limited, New Delhi | Shri Pankaj Aggarwal Shri Mukesh Sinha (*Alternate*) |
| Shaktiman Extrusions Pvt Ltd, Perumbavoor | Shri N.SureshShri T.S. Manoj (*Alternate*) |
| Supreme Industries Limited, Jalgaon | Shri G. K. Saxena |
| Tamil Nadu Water Supply & Drainage Board, Chennai | Engineering Director Joint Chief Engineer (COM) (*Alternate*) |
| Tata Consulting Engineers Ltd, Mumbai | **Representative**  |
| In Personal Capacity (*A-59, Sector 35,* *Noida 201301*) | Shri Kanwar A. Singh |
| In Personal Capacity (L-202 Metrozone, Anna Nagar West Chennai 600040) | Shri G.K. Srinivasan  |
| BIS Directorate General | Shri Sanjay pant, Scientist ‘F’ And Head (CED)[Representing Director General (Ex-officio)] |
| Member SecretaryShrimati Madhurima MadhavScientist ‘D’ (Civil Engg), BIS |

Composition of Polyolefins and GRP Piping System Subcommittee, CED 50:1

| *Organization* | *Representative(s)* |
| --- | --- |
| In Personal Capacity (*A-59, Sector 35,* *Noida 201301*) | Shri Kanwar A. Singh (*Convener*) |
| Alom Poly Extrusion Ltd, Kolkata | Shri Arnav JhunjhunwalaShri Anik Kumar Chowdhury (*Alternate*) |
| Assam Gas Company Limited, Dibrugarh | Shri Surjaya TamulikShri Ahijit Baruah (*Alternate*)  |
| Bhimrajka Impex Limited, Mumbai | Shri Vinod Bhimrajka (*Alternate*) |
| Central Ground Water Board, Faridabad | Shri D. N. ArunShri K. R. Biswas (*Alternate*)  |
| Central Institute of Plastics Engineering & Technology, Chennai | Dr K. PrakalathanDr A. K. Mohapatra (*Alternate*) |
| Central Public Works Department, New Delhi | Shri M. K. Sharma (CSQ)Shri Amar Singh (*Alternate*) |
| CSIR-National Environmental Engineering Research Institute, Nagpur | Dr (Smt) Abha SargaonkarDr Ritesh Vijay (*Alternate*) |
| Chennai Water Supply & Sewerage Board, Chennai | Engineering Director Chief Engineer (O&M) (*Alternate*) |
| Delhi Jal Board, New Delhi | Shri Y. K. Sharma Shri S. L. Meena (*Alternate*) |
| Duraline India Pvt Ltd, Mumbai | Shri Rajeev Chaturvedi Shri Sunil Saxena(*Alternate*) |
| Engineers India Ltd, New Delhi | Shri N. KaulShri R. B. Bhutda (*Alternate*) |
| EPP Composite Pipes, Rajkot  | Shri Jayraj Shah Smt Seema Vaifya (*Alternate*) |
| GAIL India Limited, New Delhi | Dr Debasish Roy Shri Manish Khandelwal (*Alternate*)Shri Nitin Gupta (Alternate II) |
| Godavari Polymers Pvt Limited, Secunderabad | Shri C. Venkateshwar Rao Shri G. Sridhar Rao (*Alternate*) |
| Government E-Marketplace, New Delh | **Representative**  |
| Indraprastha Gas Limited, New Delhi | **Representative**  |
| Industrial Toxicology Research Centre, Lucknow | Dr V. P. Sharma Dr Virendra Misra (*Alternate*) |
| In personal capacity, Navi Mumbai | Shri V. K. Sharma |
| Jain Irrigation Systems Limited, Jalgaon  | Shri M. R. Kharul Shri M. D. Chaudhari (*Alternate*) |
| Kimplas Piping Systems Ltd, Nashik  | Shri Kiran Sarode Shri Santosh Kumar (*Alternate*) |
| KITEC Industries India Limited, Mumbai | Shri Dalip V. Kolhe Shri Manoranjan G. Choudhary (*Alternate*) |
| Mahanagar Gas Limited, Mumbai | Shri K. VenugopalSmt Neha Kharya (*Alternate*) |
| Mahanagar Telephone Nigam Limited, New Delhi | Chief Engineer (BW)  |
| Maruthi Tubes Pvt Ltd, Secunderabad | Shri Manchaala Raghavendra Shri M. Nagesh Kumar (*Alternate*) |
| Military Engineer Services, Engineer- in-Chief's Branch, Integrated HQ of MoD (Army), New Delhi  | Shri A. K. DubeyShri R. K. Chauhan (*Alternate*) |
| National Test House, Kolkata | Shri S. P. KaliaShri M. M. Pabalkar (*Alternate*) |
| Ori-Plast Limited, Kolkata | Shri Ashish Agarwal Shri Somnath Mukherjee (*Alternate*)  |
| Public Health & Municipal Engineering Department, Hyderabad | Shri K. Suresh Kumar Shri Ch. Mallikarjunudu (*Alternate*) |
| Reliance Industries Limited, Mumbai | Shri S. V. RajuShri Saurabh Baghal (*Alternate* -)Shri Tushar Dongre (*Alternate* -II) |
| Sangir Plastics Pvt. Ltd., Mumbai | Shri Prashant TrivediShri K. V. C. Dora (*Alternate*) |
| In Personal Capacity (*Panchjyot CHS; H-23/01*  *Sector 29, Vashi, Navi Mumbai 400703*) | Shri V. K. Sharma |

Working Group for Preparation of Drafts for Multilayer (PE-AL-PE) Plastics Piping Systems for Indoor Gas Installations and Hot and Cold Water Supplies

|  |  |
| --- | --- |
| *Organization* | *Representative(s)* |
| In Personal Capacity (*A-59, Sector 35, Noida 201301*) | Shri Kanwar A. Singh(***Co-ordinator)*** |
| KITEC Industries India Limited, Silvasa | Shri Manoranjan Choudhary |
| NSF Safety and Certification India Pvt Ltd, Gurugram | Shri B. B. Singh |
| Plastindia Foundation Mumbai | Dr E. Sundaresan |
| Mahanagar Gas Limited, Mumbai | Shri V. Subramanian |
| Jindal MLC Pipes Pvt Ltd, New Delhi | Shri Sunil Malik |
| Indraprastha Gas Limited, New Delhi | Shri Pankaj Sharma |
| In Personal Capacity, Mumbai | Shri S. Tambrapani |