IS XXXX:XXXX

Doc: CED 50 (15770)

भारतीय मानक

बोरवेल/नलकूप के लिए असुघटियत पॉलीविनॉयल क्लोराइड

(पीवीसी-यू) के चूड़ीदार कॉलम पाइप — विशिष्टि

Indian Standard

UNPLASTICIZED POLYVINYL CHLORIDE (PVC-U) THREADED COLUMN PIPES FOR BOREWELLS/TUBEWELLS ― SPECIFICATION

ICS No. 23.040.20

© BIS 2023

BUREAU OF INDIAN STANDARDS

MANAK BHAVAN, 9, BAHADUR SHAH ZAFAR MARG

NEW DELHI 110 002

April 2023                                                                                                                                           Price Group

# Plastic Piping System Sectional Committee, CED 50

# FOREWORD

This Indian Standard was adopted by the Bureau of Indian Standards, after the draft finalized by the Plastic Piping System Sectional Committee had been approved by the Civil Engineering Division Council.

This Indian Standard has been formulated to cover requirements and test methods for unplasticized polyvinyl chloride (PVC-U) threaded column pipes for use with jet and submersible pumps in borewells/tubewells.

It is the responsibility of the purchaser or the supplier to make the appropriate selection of pipes taking into account their particular requirements and any relevant national guidelines or regulations. Relevant guidelines for installation practices should be followed.

The composition of the committee responsible for the formulation of this standard is listed in Annex C.

For the purpose of deciding whether a particular requirement of the standard is complied with the final value observed or calculated, expressing the result of a test or analysis, shall be rounded off in accordance with IS 2 : 2022 ‘Rules for rounding off numerical values (second revision)’. The number of significant places retained in the rounded off value should be the same as that of the specified value in this standard.

Indian Standard

UNPLASTICIZED POLYVINYL CHLORIDE (PVC-U)

THREADED COLUMN PIPES FOR

BOREWELLS/TUBEWELLS — SPECIFICATION

1 SCOPE

  - This standard covers the requirements of unplasticized polyvinyl chloride (PVC-U) threaded column pipes of the following types and sizes, for use with jet or submersible pumps in borewells/tubewells for water supply:

- Bell ended (socketed) type with external thread at spigot end and internal thread at bell (socket) end, of nominal sizes 25 mm, 32 mm and 40 mm; and

- Coupler joint type with external threads at both ends, connected with coupler, of nominal sizes 25 mm to 150 mm.

  - These pipes are recommended for water temperatures ranging from 1 °C to 45 °C.

- REFERENCES

The standards listed below, contain provisions, which through reference in this text, constitute provisions of this standard. At the time of publication, the editions indicated were valid. All standards are subject to revision and parties to agreements based on this standard are encouraged to investigate the possibility of applying the most recent editions of the standards listed below:

IS No.

| IS No. |  | Title |  |
| --- | --- | --- | --- |
| IS 4669 : 1968 |  | Methods of tests for polyvinyl chloride resins |  |  |
| IS 4905 : 2015 /ISO 24153 : 2009 |  | Random sampling and randomization procedures (first revision) |  |  |
| IS 4985 : 2021 |  | PVC pipes for water supplies — Specification (fourth revision) |  |  |
| IS 5382 : 2018 /ISO 4633 : 2015 |  | Rubber seals — Joint rings for water supply, drainage and sewerage pipelines — Specification for materials (second revision) |  |  |
| IS 10148 : 1982 |  | Positive list of constituents of polyvinyl chloride and its copolymers for safe use in contact with foodstuffs, pharmaceuticals and drinking water |  |  |
| IS 10151 : 2019 |  | Polyvinyl chloride (PVC) and its copolymers for its safe use in contact with foodstuffs, pharmaceuticals and drinking water — Specification (first revision) |  |  |
| IS 12235 |  | Thermoplastics pipes and fittings — Methods of test: (first revision) |  |  |
| (Part 1) : 2004 |  | Measurement of dimensions |  |  |
| (Part 2) : 2004 |  | Determination of vicat softening temperature |  |  |
| (Part 4) : 2004 |  | Determining the detrimental effect on the composition of water |  |  |
| (Part 8/Sec 1) : 2004 |  | Resistance to internal hydrostatic pressure, Section 1 Resistance to internal hydrostatic pressure at constant internal water pressure |  |  |
| (Part 9) : 2004 |  | Resistance to external blows (impact resistance) at 0 °C (round the-clock method) |  |  |
| (Part 10) : 2004 |  | Determination of organotin as tin aqueous solution |  |  |
| (Part 11) : 2004 |  | Resistance to dichloromethane at specified temperature |  |  |
| (Part 13) : 2004 |  | Determination of tensile strength and elongation |  |  |
| (Part 14) : 2004 |  | Determination of density/relative density (specific gravity) |  |  |
| (Part 19) : 2004 |  | Flattening test |  |  |

3 TERMINOLOGY

For the purpose of this standard, the following definitions shall apply:

3.1 Column Pipes — Pipes with external threads at both ends, or with external thread at one end and internal thread at the other end, for carrying out ground water with jet/submersible pump from borewell/tubewell.

3.2 Column Pipe Couplers — Cut piece of pipe with internal threads at both ends to assemble/join the column pipes.

3.3 Bell End Pipes — Pipes with bell and spigot end, in which female (internal) thread is provided at bell end and male (external) thread at spigot end for connection of pipes.

3.4 Nominal Size (DN) — The numerical designation for the size of the pipe other than a pipe designated by thread size, which is a convenient round number approximately equal to the manufactured dimension, in mm.

3.5 Nominal Outer Diameter (do) — The specified outside diameter, in mm, assigned to a nominal size.

3.6 Mean Outer Diameter (dem) — The quotient of the outer circumference of a pipe and 3.142 (π) in any cross-section, rounded off to the next higher 0.1 mm.

3.7 Minimum Mean Outer Diameter (dem, Min) — The minimum value for the mean outside diameter as specified for a given nominal size.

3.8 Maximum Mean Outer Diameter (dem, Max) — The maximum value for the mean outside diameter as specified for a given nominal size.

3.9 Outer Diameter at Any Point (de) — The value of the measurement of the outer diameter of a pipe through its cross-section at any point of the pipe, rounded off to next higher 0.1 mm.

3.10 Out-of-Roundness (Ovality) — The difference between the measured maximum and the measured minimum outside diameter in the same cross-section of the pipe.

3.11 Nominal Wall Thickness (ene and enb) — A numerical designation of the wall thickness of a component which is a convenient round number, approximately equal to the manufacturing dimensions, in mm.

NOTE — enb and ene are nominal wall thickness of barrel (thin portion) and end side (thick portion), respectively.

3.12 Wall Thickness at Any Point (ee and eb) — The value of the measurement of the wall thickness at any point around the circumference of the pipe, rounded off to the next higher 0.1 mm.

NOTE — eb and ee are wall thickness at any point of barrel (thin portion) and end side (thick portion), respectively.

3.13 Mean Wall Thickness (eme and emb) — The arithmetical mean of at least four measurements regularly spaced around the circumference and in the same cross-section of the pipe, including the measured minimum and the measured maximum values of the wall thickness in that cross-section and rounded off to the next higher 0.1 mm.

NOTE — emb and eme are mean wall thickness of barrel (thin portion) and end side (thick portion), respectively.

3.14 Tolerance — The permitted variation of the specified value of a quantity, expressed as the difference between the permitted maximum and the permitted minimum value.

3.15 Working Pressure (PN) — The numerical designation of a pipe related to the mechanical characteristics of that pipe used for reference purposes. For plastic piping systems, it corresponds to the allowable operating pressure, in MPa, conveying water at 27 °C.

3.16 Allowable Operating Pressure (PFA) — The maximum hydrostatic pressure excluding surge which is allowed in continuous use with water within the temperature range concerned. It is calculated using the following equation:

PFA = fT x PN

where

fT = derating factor depending on water temperature; and

PN  = working pressure.

NOTE — In cases where a further derating (or uprating) factor depending on the application is required,

PFA = fA x fT x PN

where

fA = factor depending on the application.

3.17 Hydrostatic Stress (σ) — The stress induced in the wall of a pipe when a pressure is applied using water as a medium. The hydrostatic stress is related to the applied pressure, P, the wall thickness of thin portion at any point, eb, and the mean outside diameter, dem, of a pipe and calculated using the following approximation equation:

σ=Pdem-ebeb2ebeb

where σ and P are in same units.

4 COMPOSITION

4.1 The material from which the pipe is produced shall consist substantially of unplasticized polyvinyl chloride to which may be added only those additives that are needed to facilitate production of sound and durable pipe of good surface finish and mechanical strength under conditions of use. None of these additives shall be used, separately or together, in quantities sufficient to constitute a toxic, organoleptic or microbial growth hazard or to materially impair the fabrication or welding properties of the pipe, or to impair the chemical, physical or mechanical properties (in particular long-term mechanical strength and impact strength) as defined in this standard. The additives to be used shall be selected from IS 10148 and shall be uniformly dispersed.

4.1.1 The monomer content (VCM content) in the resin shall be within the limits specified in 4.4.1 of IS 10151, when tested as per Annex A of IS 10151.

4.1.2 The composition shall be based on PVC resin having a K-value of 64 or greater, when tested in accordance with IS 4669.

NOTE — A test report or certificate of conformity may be obtained from the manufacturer for the VCM content (see 4.1.1) and K-value (see 4.1.2) of the resin being used, unless the same is tested in an independent laboratory. The frequency of this test report or certificate of conformity shall be once in every three months.

4.2 The addition of not more than 5 percent of the manufacturer’s own rework material conforming to this standard is permissible. No other rework material shall be used.

5 COLOUR

The pipe and coupler shall be of regular ivory white colour throughout. Slight colour deviation is permissible.

6 CLASSIFICATION

The pipes shall be classified by pressure ratings (working pressures) at 27 °C as per Table 1. The maximum permissible hydraulic head of different classes of column pipes shall be as given in Table 1.

Table 1  Classification of Column Pipes

(Clause 6)

| Sl No. | Class | Working Pressure (PN) | Maximum Permissible Hydraulic Head |
| --- | --- | --- | --- |
|  |  | MPa (kg/cm2) | m |
| (1) | (2) | (3) | (4) |
| i) | Class 1 | 1.0 (10) | 100 |
| ii) | Class 2 | 1.25 (12.5) | 125 |
| iii) | Class 3 | 1.5 (15) | 150 |
| iv) | Class 4 | 2.0 (20) | 200 |
| v) | Class 5 | 2.5 (25) | 250 |
| vi) | Class 6 | 3.5 (35) | 350 |
| vii) | Class 7 | 4.0 (40) | 400 |

The maximum safe working stress considered is 14 MPa at 27 °C.

7 DIMENSIONS

7.1.1 The diameters and wall thicknesses of unthreaded column pipes with thick-thin portion shall be as given in Table 2 and Table 3 read with Fig. 1A and Fig. 1B. The dimensional details of unthreaded column pipe couplers shall be as given in Table 4 read with Fig. 1C. The design (c and d in Fig. 1C) and number of ribs shall be as agreed between the manufacturer and the purchaser so as to ensure proper gripping during installation. The square threads on column pipes and column pipe couplers shall be as shown in Fig. 1D and Fig. 1E, respectively read with Tables 5 and 6. However, the assembly/jointing design (sealing ring/groove) shown in these figures are typical. The dimensional details of bell-ended pipes shall be as given in Table 7 read with Fig. 2. Belling dimensions of pipe shall be as per manufacturer’s design or as per the mutual agreement between the manufacturer and the purchaser.

7.1.2 Mean outer diameter and outer diameter at any point of unthreaded column pipes shall be measured according to IS 12235 (Part 1). The pipe diameter shall be measured at the thick end portion of the pipe.

7.1.3 Wall thickness of unthreaded column pipes shall be measured in accordance with the method given in IS 12235 (Part 1).

7.1.4 Nominal effective length of column pipe shall be minimum 3 000 mm. The pipes may be supplied in other lengths where so agreed upon between the manufacturer and the purchaser.

1A Unthreaded Pipe

1B Threaded Pipe

1C Ribbed Coupler Before Threading

NOTE The assembly/jointing design shown in the figure is typical.

1D Thread Profile of Column Pipe

All dimensions in millimetres.

NOTE — The assembly/jointing design shown in the figure is typical.

1E Thread Profile of Column Pipe Couplers

Fig. 1 Coupler Jointed Threaded Column Pipes

Table 2 Outer Diameter of Unthreaded Column Pipes

(Clause 7.1.1)

All dimensions in millimetres.

| Sl No. | Nominal Size DN | Mean Outer Diameter of Pipe, dem |  | Outer Diameter at any Point, de |  |
| --- | --- | --- | --- | --- | --- |
| (1) | (2) | Min (3) | Max (4) | Min (5) | Max (6) |
| i) | 25 | 33.0 | 33.3 | 32.8 | 33.5 |
| ii) | 32 | 42.0 | 42.3 | 41.8 | 42.5 |
| iii) | 40 | 48.0 | 48.3 | 47.8 | 48.5 |
| iv) | 50 | 60.0 | 60.3 | 59.8 | 60.5 |
| v) | 65 | 75.0 | 75.3 | 74.8 | 75.6 |
| vi) | 80 | 88.0 | 88.4 | 87.8 | 88.6 |
| vii) | 100 | 113.0 | 113.4 | 112.8 | 113.6 |
| viii) | 125 | 140.0 | 140.4 | 139.8 | 140.6 |
| ix) | 150 | 165.0 | 165.4 | 164.8 | 165.6 |

Table 3 Wall Thickness of Different Classes of Unthreaded Column Pipes with Thick-Thin Portion

(Clause 7.1.1)

| Sl No. |  | Nominal Size DN |  | Class of Pipe |  | Both End (Thick) Portion |  |  |  | Barrel (Thin) Portion |  |  |  | Length of Thick Portion at Both Side (L1 and L3), Min |  |  | Induced Stress, Min |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (1) |  | mm (2) |  | mm (3) |  | Min mm (4) |  | Max mm (5) |  | Min mm (6) |  |  | Max mm (7) | mm (8) |  |  | MPa (9) |
| i) |  | 25 |  | Class 1 |  | 2.9 |  | 3.30 |  | 1.50 |  |  | 1.80 | 150 |  |  | 12 |
|  |  |  |  | Class 2 |  | 3.3 |  | 3.80 |  | 1.70 |  |  | 2.00 | 150 |  |  | 12 |
|  |  |  |  | Class 3 |  | 3.8 |  | 4.40 |  | 1.90 |  |  | 2.20 | 150 |  |  | 13 |
|  |  |  |  | Class 4 |  | 4.6 |  | 5.30 |  | 2.40 |  |  | 2.80 | 150 |  |  | 13 |
| ii) |  | 32 |  | Class 1 |  | 3.3 |  | 3.80 |  | 1.50 |  |  | 1.80 | 180 |  |  | 14 |
|  |  |  |  | Class 2 |  | 3.7 |  | 4.30 |  | 1.80 |  |  | 2.10 | 180 |  |  | 14 |
|  |  |  |  | Class 3 |  | 4.3 |  | 5.00 |  | 2.20 |  |  | 2.50 | 180 |  |  | 14 |
|  |  |  |  | Class 4 |  | 5.40 |  | 6.20 |  | 2.80 |  |  | 3.20 | 180 |  |  | 14 |
|  |  |  |  | Class 5 |  | 6.50 |  | 7.50 |  | 3.50 |  |  | 4.00 | 180 |  |  | 14 |
|  |  |  |  | Class 6 |  | 8.30 |  | 9.60 |  | 4.70 |  |  | 5.40 | 180 |  |  | 14 |
|  |  |  |  | Class 7 |  | 8.50 |  | 9.80 |  | 5.80 |  |  | 6.70 | 200 |  |  | 14 |
| iii) |  | 40 |  | Class 1 |  | 3.50 |  | 4.00 |  | 1.70 |  |  | 2.00 | 180 |  |  | 14 |
|  |  |  |  | Class 2 |  | 4.10 |  | 4.70 |  | 2.10 |  |  | 2.40 | 180 |  |  | 14 |
|  |  |  |  | Class 3 |  | 4.90 |  | 5.70 |  | 2.50 |  |  | 2.90 | 180 |  |  | 14 |
|  |  |  |  | Class 4 |  | 5.90 |  | 6.80 |  | 3.20 |  |  | 3.70 | 180 |  |  | 14 |
|  |  |  |  | Class 5 |  | 7.20 |  | 8.30 |  | 4.00 |  |  | 4.60 | 180 |  |  | 14 |
|  |  |  |  | Class 6 |  | 9.30 |  | 10.70 |  | 5.40 |  |  | 6.20 | 180 |  |  | 14 |
|  |  |  |  | Class 7 |  | 9.60 |  | 11.00 |  | 6.50 |  |  | 7.50 | 200 |  |  | 14 |
| iv) | 50 |  | Class 1 |  | 4.20 |  | 4.90 |  | 2.10 |  | 2.40 | 180 |  |  | 14 |
|  |  |  | Class 2 |  | 4.90 |  | 5.60 |  | 2.60 |  | 3.00 | 180 |  |  | 14 |
|  |  |  | Class 3 |  | 5.90 |  | 6.80 |  | 3.10 |  | 3.60 | 180 |  |  | 14 |
|  |  |  | Class 4 |  | 7.20 |  | 8.30 |  | 4.00 |  | 4.60 | 200 |  |  | 14 |
|  |  |  | Class 5 |  | 8.80 |  | 10.10 |  | 5.00 |  | 5.80 | 200 |  |  | 14 |
|  |  |  | Class 6 |  | 11.10 |  | 12.80 |  | 6.70 |  | 7.70 | 200 |  |  | 14 |
|  |  |  | Class 7 |  | 11.30 |  | 13.00 |  | 8.20 |  | 9.20 | 200 |  |  | 14 |
| v) |  | 65 |  | Class 1 |  | 5.00 |  | 5.80 |  | 2.60 |  |  | 3.00 | 180 |  |  | 14 |
|  |  |  |  | Class 2 |  | 6.00 |  | 6.90 |  | 3.30 |  |  | 3.80 | 180 |  |  | 14 |
|  |  |  |  | Class 3 |  | 7.00 |  | 8.10 |  | 3.90 |  |  | 4.50 | 180 |  |  | 14 |
|  |  |  |  | Class 4 |  | 8.60 |  | 9.90 |  | 5.00 |  |  | 5.80 | 200 |  |  | 14 |
|  |  |  |  | Class 5 |  | 10.40 |  | 12.00 |  | 6.20 |  |  | 7.10 | 200 |  |  | 14 |
|  |  |  |  | Class 6 |  | 13.50 |  | 15.50 |  | 8.40 |  |  | 9.70 | 200 |  |  | 14 |
| vi) |  | 80 |  | Class 1 |  | 5.60 |  | 6.40 |  | 3.10 |  |  | 3.60 | 180 |  |  | 14 |
|  |  |  |  | Class 2 |  | 6.50 |  | 7.50 |  | 3.80 |  |  | 4.40 | 180 |  |  | 14 |
|  |  |  |  | Class 3 |  | 7.90 |  | 9.10 |  | 4.50 |  |  | 5.20 | 180 |  |  | 14 |
|  |  |  |  | Class 4 |  | 9.70 |  | 11.20 |  | 5.90 |  |  | 6.80 | 200 |  |  | 14 |
|  |  |  |  | Class 5 |  | 11.60 |  | 13.30 |  | 7.30 |  |  | 8.40 | 200 |  |  | 14 |
|  |  |  |  | Class 6 |  | 15.20 |  | 17.50 |  | 9.80 |  |  | 11.30 | 200 |  |  | 14 |
| vii) |  | 100 |  | Class 1 |  | 6.80 |  | 7.80 |  | 3.90 |  |  | 4.50 | 180 |  |  | 14 |
|  |  |  |  | Class 2 |  | 8.20 |  | 9.40 |  | 4.90 |  |  | 5.70 | 180 |  |  | 14 |
|  |  |  |  | Class 3 |  | 9.60 |  | 11.00 |  | 5.80 |  |  | 6.70 | 180 |  |  | 14 |
|  |  |  |  | Class 4 |  | 11.90 |  | 13.70 |  | 7.60 |  |  | 8.60 | 200 |  |  | 14 |
|  |  |  |  | Class 5 |  | 14.30 |  | 16.50 |  | 9.30 |  |  | 10.70 | 200 |  |  | 14 |
|  |  |  |  | Class 6 |  | 19.00 |  | 21.90 |  | 12.60 |  |  | 14.50 | 200 |  |  | 14 |
| viii) |  | 125 |  | Class 1 |  | 8.20 |  | 9.40 |  | 4.90 |  |  | 5.60 | 230 |  |  | 14 |
|  |  |  |  | Class 2 |  | 9.70 |  | 11.20 |  | 6.00 |  |  | 6.90 | 230 |  |  | 14 |
|  |  |  |  | Class 3 |  | 11.50 |  | 13.20 |  | 7.20 |  |  | 8.30 | 230 |  |  | 14 |
|  |  |  |  | Class 4 |  | 14.40 |  | 16.60 |  | 9.40 |  |  | 10.80 | 250 |  |  | 14 |
|  |  |  |  | Class 5 |  | 17.30 |  | 19.90 |  | 11.50 |  |  | 13.20 | 250 |  |  | 14 |
|  |  |  |  | Class 6 |  | 23.00 |  | 26.50 |  | 15.60 |  |  | 18.00 | 250 |  |  | 14 |
| ix) |  | 150 |  | Class 1 |  | 9.30 |  | 10.70 |  | 5.70 |  |  | 6.60 | 230 |  |  | 14 |
|  |  |  |  | Class 2 |  | 11.20 |  | 12.90 |  | 7.10 |  |  | 8.20 | 230 |  |  | 14 |
|  |  |  |  | Class 3 |  | 13.10 |  | 15.10 |  | 8.40 |  |  | 9.70 | 230 |  |  | 14 |
|  |  |  |  | Class 4 |  | 16.60 |  | 19.10 |  | 11.00 |  |  | 12.70 | 250 |  |  | 14 |
|  |  |  |  | Class 5 |  | 20.10 |  | 23.10 |  | 13.60 |  |  | 15.70 | 250 |  |  | 14 |
|  |  |  |  | Class 6 |  | 26.90 |  | 31.00 |  | 18.40 |  |  | 21.20 | 250 |  |  | 14 |
| NOTE — Length of thick portion (L1 and L3) at both ends of the pipe is required for thread operation for joining the pipes with each other with couplers. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Table 4 Dimensional Details of Column Pipe Couplers

(Clause 7.1.1)

All dimensions in millimetres

| Sl No. | Nominal Size DN | Mean Outer Diameter of Column Pipe Coupler, a, Min |  | Internal Diameter of Column Pipe Coupler, b, Max |
| --- | --- | --- | --- | --- |
|  |  | For classes 1 to 3 | For classes 4 to 7 |  |
| (1) | (2) | (3) | (4) | (5) |
| i) | 25 | 45.0 | 51.0 | 29.0 |
| ii) | 32 | 55.0 | 60.0 | 38.0 |
| iii) | 40 | 62.0 | 72.0 | 44.0 |
| iv) | 50 | 80.0 | 86.0 | 55.0 |
| v) | 65 | 92.0 | 99.0 | 70.0 |
| vi) | 80 | 108.0 | 115.0 | 83.0 |
| vii) | 100 | 136 | 145.0 | 108.0 |
| viii) | 125 | 165 | 175.0 | 134.0 |
| ix) | 150 | 190 | 205.0 | 159.0 |

TABLE 4 DIMENSIONAL DETAILS OF COLUMN PIPE COUPLERS

(Clause 7.1.1)

Fig. 2 Bell Ended Column Pipes with Internal Threads at One End and Spigot at Another End with External Threads

8 THREADING OF COLUMN PIPES AND COUPLERS

8.1 Column Pipes

Pipes with external threads at both ends shall be used with couplers. Bell end pipes shall have external threads at one end and internal threads at the other end.

8.2 Column Couplers

Column couplers shall have internal threads at both ends.

8.3 Pipes shall have basic thread dimensions as given in Table 5 read with Fig. 1D.  Couplers shall have basic thread dimensions as given in Table 6 read with Fig. 1E.

8.4 Sealing rings and elements made of elastomeric material such as EPDM, and of appropriate dimensions ensuring secure fit, shall be used to seal the joint. These sealing materials shall be of hardness class 60 IRHD/Shore A as per IS 5382. The design of the profile of the sealing ring is left to the manufacturer as long as the pipe with sealing ring meets the requirements of the standard and ensures leak free installation.

NOTE — A test report or conformity certificate may be obtained from the manufacturer of the sealing ring for conformity to IS 5382. The frequency of this test report or conformity certificate shall be once in three months.

8.5 The design for the locking of permanent end pipe with coupler is left to the manufacturer as long as the pipe and coupler assembly meets the requirements of the standard and ensures leak free installation.

8.5.1 The manufacture should declare regarding the use of adhesive/solvent if any. Such material, when used, shall not have any detrimental effect on the quality of  water for its intended use.

Table 5 Thread Dimensions for Both Male Ends of Column Pipe

(Clause 7.1.1 and 8.3)

| All dimensions in millimetres |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sl No. | Nominal Size, DN | Male End (Tolerance-0.3+0.0) |  | Free End Side Length, Min |  | Permanent End Side Length, Min |  | Pitch |
|  |  | Major Diameter | Minor Diameter | Lf | lf | Lp | lp |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |
| i) | 25 | 32.80 | 30.80 | 56.0 | 3.0 | 60.0 | 12 | 3.0 |
| ii) | 32 | 41.50 | 39.50 | 56.0 | 3.0 | 60.0 | 12 | 3.0 |
| iii) | 40 | 47.50 | 45.50 | 56.0 | 3.0 | 60.0 | 12 | 3.0 |
| iv) | 50 | 59.50 | 56.50 | 64.0 | 3.5 | 80.0 | 12 | 4.0 |
| v) | 65 | 74.50 | 71.50 | 64.0 | 3.5 | 80.0 | 12 | 4.0 |
| vi) | 80 | 87.50 | 84.30 | 64.0 | 3.5 | 85.0 | 14 | 4.0 |
| vii) | 100 | 112.50 | 109.10 | 74.0 | 5.0 | 85.0 | 14 | 6.0 |
| viii) | 125 | 139.50 | 135.50 | 84.0 | 5.0 | 104.0 | 14 | 6.0 |
| ix) |  | 150 |  | 164.50 |  | 160.50 |  | 84.0 |  | 5.0 |  | 104.0 |  | 14 |  | 6.0 |  |

Table 6 Thread Dimensions for Both Female Ends of

Column Pipe Coupler

(Clause 7.1.1 and 8.3)

All dimensions in millimetres

| Sl No. | Nominal Size, DN | Female End (Tolerance-0.0+0.3) |  | Free End Side Length, Min |  | Permanent End Side Length, Min |  | Pitch |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Major Diameter | Minor Diameter | Lf | lf | Lp | lp |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |
| i) | 25 | 33.20 | 31.20 | 60.0 | 15 | 51.0 | 14 | 3.0 |
| ii) | 32 | 41.90 | 39.90 | 60.6 | 15 | 51.0 | 14 | 3.0 |
| iii) | 40 | 47.90 | 45.90 | 60.6 | 15 | 51.6 | 14 | 3.0 |
| iv) | 50 | 60.00 | 57.00 | 66.3 | 15 | 72.3 | 14 | 4.0 |
| v) | 65 | 75.00 | 72.00 | 66.3 | 15 | 72.3 | 14 | 4.0 |
| vi) | 80 | 88.20 | 85.00 | 66.3 | 15 | 77.3 | 14 | 4.0 |
| vii) | 100 | 113.30 | 109.90 | 76.8 | 15 | 77.8 | 14 | 6.0 |
| viii) | 125 | 140.30 | 136.30 | 86.8 | 15 | 95.8 | 14 | 6.0 |
| ix) | 150 | 165.30 | 161.30 | 86.8 | 15 | 95.8 | 14 | 6.0 |

Table 7 Dimensions of Bell-Ended Pipes

(Clause 7.1.1)

All dimensions in millimetres

| Sl No. |  | Nominal Size, DN |  | D-0.0+0.2 |  | D1-0.2+0.0 |  | D2 -0.2+0.0 |  | Major d -0.2+0.0 |  | Minor d -0.0+0.2 |  | A -0.0+2.0 |  | B -0.0+2.0 |  |  | C -0.0+2.0 | E -0.2+0.0 | F -0.2+0.0 | G -0.0+0.1 | H -0.2+0.0 | Thread Depth | Pitch |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) |
| i) | 25 | 35.2 | 30.6 | 31.1 | 32.8 | 31.2 | 8 | 51 | 60 | 12 | 48 | 2.5 | 3.0 | 1.0 | 3.0 |
| ii) | 32 | 43.4 | 39.3 | 39.8 | 41.5 | 39.9 | 8 | 51 | 60 | 12 | 48 | 2.5 | 3.0 | 1.0 | 3.0 |
| iii) |  | 40 |  | 49.4 |  | 45.3 |  | 45.8 |  | 47.5 |  | 45.9 |  | 8 |  | 51 |  |  | 60 | 12 | 48 | 2.5 | 3.0 | 1.0 | 3.0 |

9 TESTS

9.1 Visual Appearance

The internal and external surfaces of the pipe shall be smooth, clean and free from other defects. Slight shallow longitudinal grooves or irregularities in the wall thickness shall be permissible provided the pipe dimensions remain within permissible limits. The ends shall be clean, smoothly cut and reasonably square to the axis of the pipe.

9.2 Resistance to External Blows at 0 °C

When tested by the method described in IS 12235 (Part 9), the pipe shall have a true impact rate of not more than 10 percent. The total mass of the striker and height of free fall shall correspond to the values given in Table 8.

Table 8 Total Mass of Striker and Height of Free Fall for Resistance

to External Blows Test

(Clause 9.2)

| Sl No. | Nominal Size DN | Total Mass of Striker kg | Height of Free Fall mm | Number of Equidistant Lines to be Drawn (No.) |
| --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) |
| i) | 25 | (0.25 ± 0.5) % | 1 000 ± 10 | 1 |
| ii) | 32 | (0.25 ± 0.5) % | 1 000 ± 10 | 1 |
| iii) | 40 | (0.25 ± 0.5) % | 1 000 ± 10 | 3 |
| iv) | 50 | (0.25 ± 0.5) % | 2 000 ± 10 | 3 |
| v) | 65 | (0.25 ± 0.5) % | 2 000 ± 10 | 4 |
| vi) | 80 | (0.50 ± 0.5) % | 2 000 ± 10 | 4 |
| vii) | 100 | (0.50 ± 0.5) % | 2 000 ± 10 | 6 |
| viii) | 125 | (1.00 ± 0.5) % | 2 000 ± 10 | 8 |
| ix) | 150 | (1.00 ± 0.5) % | 2 000 ± 10 | 8 |

9.3 Flattening Test

Flatten the specimens of pipe of at least 50 mm length, taken from both end (thick) and barrel (thin) portion of the pipe and that taken from the column pipe coupler, between parallel plates in a suitable press until the distance between the plates is 40 percent of the outside diameter of the pipe or the walls of the pipe touch, whichever occurs first. This test shall be carried out in accordance with the method given in IS 12235 (Part 19). The rate of the loading shall be uniform and such that the compression is completed within 2 min to 5 min. On removal of load, examine the specimen for evidence of splitting, creaking or breaking.

9.4 Tensile Strength and Elongation at Break

When tested by the method described in IS 12235 (Part 13), the average tensile strength of two test specimens cut longitudinally from barrel (thin) portion of the same pipe at maximum load shall be not less than 45 MPa and the elongation at break shall not be less than 30 percent.

NOTE — The specimen for the test shall be prepared from a section of the pipe. The specimens shall be cut or machined from lengths of pipe in the longitudinal direction, that is, along the pipe axis.

9.5 Ultimate Breaking load

Ultimate breaking load shall be checked at both sides of the threaded assembly of column socketed pipe or cut piece of thick end portion of pipe with coupler. Threaded assembly shall be fitted in suitable end fixtures. End fixtures shall then be mounted on the universal testing machine (UTM) of adequate capacity. The test temperature and test speed shall be (27 ± 2) °C and 10 mm/min, respectively.  The jaws of the UTM shall be pulled until the assembly breaks. The pick load shall be noted. Minimum pick load shall be as per Table 9 for all size and class of pipes.

NOTE — A typical ultimate breaking load assembly is shown in Fig. 3 for reference.

3A Pipe with Coupler

3B Bell and Spigot Ended Pipe

Fig. 3 Typical Ultimate Breaking Load Assembly

Table 9 Ultimate Breaking Load

(Clause 9.5)

| Sl No. | Nominal Diameter DN | Class of Pipe | Ultimate Breaking Load, Min kg |
| --- | --- | --- | --- |
| (1) | (2) | (3) | (4) |
| i) | 25 | Class 1 | 588 |
|  |  | Class 2 | 717 |
|  |  | Class 3 | 802 |
|  |  | Class 4 | 1 008 |
| ii) | 32 | Class 1 | 859 |
|  |  | Class 2 | 1 023 |
|  |  | Class 3 | 1 238 |
|  |  | Class 4 | 1 552 |
|  |  | Class 5 | 1 906 |
|  |  | Class 6 Class 7 | 2 479 2 669 |
| iii) | 40 | Class 1 | 1 113 |
|  |  | Class 2 | 1 363 |
|  |  | Class 3 | 1 609 |
|  |  | Class 4 | 2 027 |
|  |  | Class 5 | 2 489 |
|  |  | Class 6 Class 7 | 3 253 3 815 |
| iv) | 50 | Class 1 | 1 720 |
|  |  | Class 2 | 2 111 |
|  |  | Class 3 | 2 495 |
|  |  | Class 4 | 3 168 |
|  |  | Class 5 | 3 889 |
|  |  | Class 6 Class 7 | 5 050 6 007 |
| v) | 60 | Class 1 | 2 662 |
|  |  | Class 2 | 3 346 |
|  |  | Class 3 | 3 922 |
|  |  | Class 4 | 4 950 |
|  |  | Class 5 | 6 033 |
|  |  | Class 6 | 7 912 |
| vi) | 80 | Class 1 | 3 722 |
|  |  | Class 2 | 4 525 |
|  |  | Class 3 | 5 314 |
|  |  | Class 4 | 6 851 |
|  |  | Class 5 | 8 332 |
|  |  | Class 6 | 10 838 |
| vii) | 100 | Class 1 | 6 018 |
|  |  | Class 2 | 7 491 |
|  |  | Class 3 | 8 793 |
|  |  | Class 4 | 11 329 |
|  |  | Class 5 | 13 639 |
|  |  | Class 6 | 17 891 |
| viii) | 125 | Class 1 | 9 362 |
|  |  | Class 2 | 11 371 |
|  |  | Class 3 | 13 523 |
|  |  | Class 4 | 17 362 |
|  |  | Class 5 | 20 899 |
|  |  | Class 6 | 27 446 |
| ix) | 150 | Class 1 | 12 842 |
|  |  | Class 2 | 15 855 |
|  |  | Class 3 | 18 604 |
|  |  | Class 4 | 23 905 |
|  |  | Class 5 | 29 120 |
|  |  | Class 6 | 38 149 |

9.6 Izod Impact Strength Test

When tested in accordance with the method described in Annex A, the notch izod-impact strength shall not be less than 60 J/m.

9.7 Resistance to Dichloromethane Test

When tested in accordance with the method described in IS 12235 (Part 11), there shall be no attack observed on any part of the surface of test piece taken from pipe and coupler.

9.8 Density

When tested by the method described in IS 12235 (Part 14), the density of the material of the pipe and coupler shall be between 1.40 g/cm3 and 1.44 g/cm3.

9.9 Vicat Softening Temperature

The vicat softening temperature shall not be less than 80 °C when tested by the method described in IS 12235 (Part 2) for both pipe and coupler.

NOTE — The test may be done on a test piece cut from a sample of the pipe used for some other test (such as density or resistance to external blows) as long as that sample has not been subjected to conditions that could influence the vicat softening temperature.

9.10 Effect on Water

The pipes shall not have any detrimental effect on the composition of water flowing through them. When tested in accordance with the method described in IS 12235 (Part 4) and IS 12235 (Part 10), the quantities of lead, dialkyl tin C4 and higher homologues (measured as tin) and any other toxic substances extracted from the internal walls of the pipes shall not exceed the concentrations as specified in 10.3 of IS 4985 and meet the other requirements given in 10.3.1 of IS 4985.

NOTE — Implementation of the phase-out programme of the Government of India for use of lead stabilizers in PVC pipe and fitting manufacturing shall be borne in mind.

9.11 Hydrostatic Pressure Test

When subjected to internal hydrostatic pressure test in accordance with the procedure given in IS 12235 (Part 8/Sec 1), the pipe shall not fail during the prescribed test duration. The temperature and duration of the test shall conform to the requirement given in Table 10. The test shall be carried out not earlier than 24 h after the pipes have been manufactured. This test should be performed on thin barrel portion.

Table 10 Test Parameters for Internal Hydrostatic Pressure Test

(Clause 9.11)

| Sl No. | Test | Test Temperature, Min °C | Test Duration (Minimum Holding Time) h | Test Pressure, Min MPa |
| --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) |
| i) | Acceptance Test | 27 ± 2 | 1 | 2.5 X PN |

9.12 Joint Leak Pressure Test

When subjected to internal hydrostatic pressure test in accordance with the procedure given in Annex B, the representative assembly of pipe and coupler or bell end side and spigot end side of pipe sample shall withstand for 1 h without rupture, separation or leakage with an internal hydrostatic pressure of 1.5 times the working pressure (PN) at room temperature.

10 SAMPLING AND CRITERIA FOR CONFORMITY

10.1 Acceptance Tests

10.1.1 The scale of sampling and criteria for conformity of a lot for acceptance tests specified in 7, 8 and 9.1 to 9.3 shall be as given in 10.1.5 and 10.1.6 read along with Table 11 and for those specified in 9.4, 9.5, 9.7, 9.8, 9.9, 9.11 and 9.12 shall be as given under 10.1.7.

10.1.2 All pipes, in a single consignment, of the same type, same size and same class, manufactured under essentially similar conditions, shall constitute a lot.

10.1.3 For ascertaining conformity of the lot to the requirements of the specification, samples shall be tested from each lot separately.

10.1.4 The pipes shall be selected at random from the lots in order to ensure randomness of selection, a random number table shall be used. For guidance on the use of random number tables, IS 4905 may be referred to. In the absence of a random number table, the following procedure may be adopted:

Starting from any pipe in the lot, count them as 1, 2, 3, etc, up to r and so on; where r is the integral part of Nln, N being the number of pipes in the lot and n the number of pipes in the sample. Every 'r th' pipe so counted shall be withdrawn so as to constitute the required sample size.

10.1.5 The number of samples given for the first sample in col (5) of Table 11 shall be taken from the lot and examined for requirements given in 7, 8 and 9.1. A pipe failing to satisfy any of these requirements shall be considered as defective. The lot shall be deemed to have satisfied the requirements if the number of defectives found in the first sample is less than or equal to the corresponding acceptance number given in col (7). The lot shall be deemed not to have met these requirements, if the number of defectives found in the first sample is greater than or equal to the corresponding rejection number given in col (8). If, however, the number of defectives found in the first sample lies between the corresponding acceptance and rejection numbers given in col (7) and (8), a second sample of the size given in col (5) shall be taken and examined for these requirements. The lot shall be considered to have satisfied these requirements if the number of defectives found in the cumulative sample is less than or equal to the corresponding acceptance number given in col (7), otherwise not.

10.1.6 The lot, having satisfied the requirements under 10.1.5 shall be tested for the requirements in 9.2 and 9.3. For this purpose, a sub-sample from those tested under 10.1.5 shall be drawn as given in col (10) of Table 11 for the first/second sample size. The lot shall be deemed to have met the requirements given in the standard, if the number of defectives found in the first sample is less than or equal to the corresponding acceptance number given in col (12). The lot shall be deemed not to have met these requirements, if the number of defectives found in the first sample is greater than or equal to the corresponding rejection number given in col (13). If, however, the number of defectives found in the first sample lies between the corresponding acceptance and rejection numbers given in col (12) and (13), a second sample of the size given in col (10) shall be taken and tested for the requirement, the lot shall be deemed to have satisfied the requirements, if the number of defectives found in the cumulative sample is less than or equal to the corresponding acceptance number given in col (12), otherwise not.

10.1.7 The lot, having satisfied the requirements under 10.1.5 and 10.1.6, shall be tested for 9.4, 9.5, 9.7, 9.8, 9.9, 9.11 and 9.12. For this, a sub-sample of 3 pipes from each lot irrespective of the lot size shall be selected from those tested under 10.1.5 and 10.1.6. All pipes in the sub-sample shall be tested for requirements as specified in 9.4, 9.5, 9.7, 9.8, 9.9, 9.11 and 9.12. The lot shall be considered to have passed only if no failure is reported.

Table 11 Sampling and Acceptance Criteria

(Clauses 10.1.1, 10.1.5 and 10.1.6)

| Sl No. | Number of Pipes in the Lot | Nominal Size DN mm | For Tests Under 7, 8 and 9.1 |  |  |  |  | For Tests Under 9.2 and 9.3 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Sample |  | Cumulative Sample Size | Acceptance Number | Rejection Number | Sub-Sample |  |  |  | Cumulative Sample Size | Acceptance Number | Rejection Number |
|  |  |  | No. | Size |  |  |  | No. |  | Size |  |  |  |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) |  | (11) |  | (12) | (13) |
| i) | Up to 1 000 | ≤ 100 | 1st | 13 | 13 | 0 | 2 | 1st | 3 |  | 3 |  | 0 | 2 |
|  |  |  | 2nd | 13 | 26 | 1 | 2 | 2nd | 3 |  | 6 |  | 1 | 2 |
|  |  | > 100 | 1st | 5 | 5 | 0 | 2 | 1st | 3 |  | 3 |  | 0 | 2 |
|  |  |  | 2nd | 5 | 10 | 1 | 2 | 2nd | 3 |  | 6 |  | 1 | 2 |
| ii) | 1 001- 3 000 | ≤ 100 | 1st | 20 | 20 | 0 | 3 | 1st | 3 |  | 3 |  | 0 | 2 |
|  |  |  | 2nd | 20 | 40 | 3 | 4 | 2nd | 3 |  | 6 |  | 1 | 2 |
|  |  | > 100 | 1st | 8 | 8 | 0 | 2 | 1st | 3 |  | 3 |  | 0 | 2 |
|  |  |  | 2nd | 8 | 16 | 1 | 2 | 2nd | 3 |  | 6 |  | 1 | 2 |
| iii) | 3 001- 10 000 | ≤ 100 | 1st | 32 | 32 | 0 | 3 | 1st | 3 |  | 3 |  | 0 | 2 |
|  |  |  | 2nd | 32 | 64 | 3 | 4 | 2nd | 3 |  | 6 |  | 1 | 2 |
|  |  | > 100 | 1st | 13 | 13 | 0 | 3 | 1st | 3 |  | 3 |  | 0 | 2 |
|  |  |  | 2nd | 13 | 26 | 3 | 4 | 2nd | 3 |  | 6 |  | 1 | 2 |
| iv) | 10 001 and above | ≤ 100 | 1st | 50 | 50 | 2 | 5 | 1st | 6 |  | 6 |  | 0 | 2 |
|  |  |  | 2nd | 50 | 100 | 6 | 7 | 2nd | 6 |  | 12 |  | 2 | 3 |
|  |  | > 100 | 1st | 20 | 20 | 1 | 4 | 1st | 4 |  | 4 |  | 0 | 2 |
|  |  |  | 2nd | 20 | 40 | 4 | 5 | 2nd | 4 |  | 8 |  | 1 | 2 |
| NOTE ─ For test under 9.2, the numbers mentioned in col 10 to col 13 represent the number of times the test is to be carried out. They do not represent the number of pipe samples nor the number of blows nor the number of failures. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

10.2 Type Tests

These tests are intended to prove the suitability and performance of pipes whenever there is a change in the composition, size and type of pipe as well as in the method/technique in the manufacturing process. Tests specified in 9.6 and 9.10 shall be taken as type test.

10.2.1 Izod Impact Strength Test

10.2.1.1 For this type test, the manufacturer or the supplier shall furnish to the testing authority three samples of pipes of different diameters and different classes of the same type (selected preferably from a regular production lot).

10.2.1.2 Three samples so selected shall be tested for compliance with the requirements of type test as given in 9.6.

10.2.1.3 If all the three samples pass the requirements of the izod impact strength test, the type test of the pipe under consideration shall be considered to be eligible for approval, which shall be normally valid for a period of one year.

10.2.1.4 In case any of the samples fails in this test, the testing authority, at its discretion, may call for fresh samples not exceeding the original number, and subject them to the test for izod impact strength test. If, in the repeat test, no single failure occurs, the type of pipe under consideration shall be considered eligible for type approval. If any of the samples fails in the repeat test, the type of pipe shall not be approved. The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

10.2.1.5 At the end of the validity period (normally one year) or earlier, if necessary, the testing authority may call for fresh samples for izod impact strength test for the purpose of type approval.

10.2.2 Test for Effect on Water

10.2.2.1 For this type test, the manufacturer or the supplier shall furnish to the testing authority three samples of the smallest size of pipe taken from each machine (selected preferably from a regular production lot).

10.2.2.2 Three samples so selected shall be tested for compliance with the requirements for effect on water as given in 9.10.

10.2.2.3 If all three samples pass the requirements for effect on water, the type test of the pipe under consideration shall be considered to be eligible for approval, which shall be normally valid for a period of one year.

10.2.2.4 In case any of the samples fails in this test, the testing authority, at its discretion, may call for fresh samples not exceeding the original number, and subject them to the test for effect on water. If, in the repeat test, no single failure occurs, the type of pipe under consideration shall be considered eligible for type approval. If any of the samples fails in the repeat test, the type of pipe shall not be approved. The manufacturer or the supplier may be asked to improve the design and resubmit the product for type approval.

10.2.2.5 At the end of the validity period (normally one year) or earlier, if necessary, the testing authority may call for fresh samples for effect on water test for the purpose of type approval.

11 MARKING

11.1 Each pipe shall be clearly and indelibly marked in ink/paint at intervals of not more than 1 metre, and strip in colour as indicated in 11.2. The markings shall show the following:

a) Manufacturer's name or trade-mark;

b) Nominal size (DN);

c) Class of pipe and working pressure rating;

d) The phrase ‘Column Pipe’; and

e) Lot number/Batch number containing information of date of manufacture.

11.1.1 The lot number/batch number shall include the details of production in the following manner:

| Year | Month | Day | Machine No. | Shift |  |
| --- | --- | --- | --- | --- | --- |
| xxxx | xx | xx | xxx | x |  |

11.2 The information according to 11.1 and 11.1.1 shall be marked in black colour and a strip of minimum         3 mm width of colour as indicated below for different classes of pipes shall be provided. Alternatively, the information to be marked/painted can be printed in colour as given below without any strip.

| Sl No. | Class | Colour of Marking/Strip |
| --- | --- | --- |
| (1) | (2) | (3) |
| i) | Class 1 | Red |
| ii) | Class 2 | Blue |
| iii) | Class 3 | Green |
| iv) | Class 4 | Brown |
| v) | Class 5 | Yellow |
| vi) | Class 6 | Black |
| vii) | Class 7 | Pink |

11.3 BIS Certification Marking

Each column pipe and coupler conforming to the requirements of this standard may be certified as per the conformity assessment schemes under the provisions of the Bureau of Indian Standards Act, 2016 and the Rules and Regulations framed thereunder, and the pipe may be marked with the Standard Mark.

ANNEX A

(Clause 9.6)

METHOD OF TEST FOR DETENMINATION OF IZOD IMPACT STRENGTH

A-1 GENERAL

Izod impact strength is the striking energy absorbed by a notched test specimen relative to the cross-sectional area. This test is used to assess toughness or brittleness of the test specimen.

A-2 APPARATUS

Apparatus required for the test are:

- V-Notch cutting Machine; and

- Impact testing machine as per given below;

- The striker of the pendulum shall be hardened steel and shall be a cylindrical surface having a radius of curvature of (0.80 ± 0.20) mm with its axis horizontal and perpendicular to the plane of swing of the pendulum.

- The position of the pendulum holding and releasing mechanism shall be such that the vertical height of fall of the striker shall be (610 ± 2) mm. This will produce a velocity of the striker at the moment of impact of approximately 3.5 m/s.

A-3 TEST SPECIMEN

A-3.1 Shape and Size

Test specimen shall be as per Fig. 4.

Fig.4 Dimensions of Izod Test Specimen

A-3.2 Preparation

The specimen after cutting and grinding to the specified size as above shall be subjected to conditioning at temperature of (23 ± 2) ºC and (50 ± 5) percent relative humidity in the environmental test chamber for a minimum duration of 16 h. Five test specimens shall be prepared for the test from each pipe sample.

A-4 PROCEDURE

A-4.1 The test shall be conducted in the same atmosphere as that used for conditioning, unless otherwise agreed upon by the interested parties, for example for testing at high or low temperature. The test piece shall be mounted on the pendulum impact testing machine as shown in Fig. 5 and the hammer shall be released to strike on the front side of the notch of the test specimen. Striking energy absorbed by the test specimen in joule shall be indicated on the scale of the impact testing machine.

A-4.2 The test piece shall be kept in vertical position while testing the impact and before striking the specimen, the dissipation energy shall be noted by releasing the hammer without test specimen. This dissipation energy shall be subtracted from the energy absorbed by specimen during the test and the reading shall be noted as G0 joule.

Izod impact strength of the specimen shall be calculated as:

Hn= G0 ×1 000F J/m

where

Hn = Izod impact strength;

G0 = Noted energy; and

F  = Actual thickness of the specimen.

Fig. 5 Relationship of Vise, Specimen and Striking Edge to Each Other

ANNEX B

(Clause 9.12)

JOINT LEAK PRESSURE TEST

B-1 SCOPE

B-1.1 This Annex specifies the method for joint leak pressure test for the assembly of threaded pipe and coupler and threaded bell end socket and threaded spigot pipe.

B-2 TEST PIECES

B-2.1 Typical assembly of specimen for joint leak pressure test is shown in Fig. 6.

B-2.2 For the assembly of coupler type column pipe, take 2 numbers of 300 mm long cut piece of one side threaded column pipe and 1 number of threaded coupler.  Assemble 2 numbers of pipe cut piece at both end of the coupler at respective side of permanent and temporary side as shown in Fig. 6A. Seal the joint of pipe and coupler with a sealing ring as per the standard design of manufacturer for practical use.

B-2.3 For the assembly of bell type pipe, take 1 number of 300 mm long pipe having threaded bell end (female thread) at one side and other side plain and 1 number of 300 mm long pipe having spigot end (male thread) at one side and other side plain. Assemble spigot end pipe into the bell end socket as shown in Fig. 6B. Seal the joint with a sealing ring as per the standard design of manufacturer for practical use.

6A Pipe with Coupler

6B Bell and Spigot Ended Pipe

Fig. 6 Typical Assembly of Specimen for Joint Leak Pressure Test

B-3 TEST METHOD

After assembly, close both end of the pipe with suitable metal end caps. Fill the water into the assembly. This test should be performed at the floor and all precautions shall be taken for ensuring human safety. Attach assembly with hydrostatic pressure testing machine. Apply the hydrostatic pressure of 1.5 times the pressure rating (PN) for a period of 1 h. During the testing, monitor for any leakage from the coupler and pipe junction or pipe and bell end junction.

ANNEX C

(Foreword)

COMMITTEE COMPOSITION

Plastic Piping Systems Sectional Committee, CED 50

| Organization |  |  |  | Representative(s) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| In Personal Capacity (Vice Chancellor, Ravenshaw University, Cuttack 753003) | Dr S. K. Nayak (Chairperson) |
| Borouge India Pvt Ltd, Mumbai | Shri Prashant D. Nikhade |
| Brihan Mumbai Licensed Plumbers Association, Mumbai | Shri Kishor V. Merchant Shri Bijal M. Shah (Alternate) |
| Central Institute of Plastic Engineering and Technology, Chennai | Dr S. N. Yadav Shri D. Anjaneya Sharma (Alternate) |
| Central Public Health Environmental Engineering Organization, New Delhi | Dr Ramakant Shri Vipin Kumar Patel (Alternate) |
| Central Public Works Department, New Delhi | Shri M. K. Mallick Shri Divakar Agrawal (Alternate) |
| Chennai Metropolitan Water Supply & Sewerage Board, Chennai | Engineering Director Superintending Engineer (P&D) (Alternate) |
| CSIR-Central Building Research Institute, Roorkee | Dr B. Singh Shri Rajiv Kumar (Alternate) |
| CSIR-National Environmental Engineering Research Institute, Nagpur | Dr (Shrimati) Abha Sargonkar Dr Ritesh Vijay (Alternate) |
| Delhi Development Authority, New Delhi | Superintending Engineer (D) Executive Engineer (R&D) (Alternate) |
| Delhi Jal Board, New Delhi | Shri Y. K. Sharma Shri S. L. Meena (Alternate) |
| Department of Chemical & Petrochemicals Govt. of India, New Delhi |  |  |  | Joint Industrial Advisor |  |  |  |
| Finolex Industries Limited, Pune | Shri Arun Sonawane Shri D. J. Salunke (Alternate) |
| GAIL India Limited, New Delhi | Shri Manish Khandelwal Shri Kuldeep Negi (Alternate I) Shri Nitin Gupta (Alternate II) |
| Haldia Petrochemicals Ltd, Kolkata | Shri Raj K. Datta Shri Amartya Maity (Alternate) |
| HPCL – Mittal Energy Ltd, Noida | Shri Vineet Kumar Gupta Shri Alakesh Ghosh (Alternate) |
| HSIL Ltd (Pipe Divison), Hyderabad | Shri Tushar Lokare Shri Vinoy Kumar (Alternate) |
| Indian Oil Corporation Ltd, Panipat | Shri Sumit Basu Shri Raja Poddar (Alternate I) Shri Naveen Garg (Alternate II) |
| Jain Irrigation System Limited, Jalgaon | Shri S. Narayanaswami Shri P. H. Chaudhari (Alternate) |
| Mahindra EPC Irrigation Ltd, Nashik | Shri Sankar Kumar Maiti Shri Ashish Kumar (Alternate) |
| Military Engineer Services, Engineer-in-Chief's Branch, Integrated HQ of MoD (Army), New Delhi | Shri N. K. Goel Shri Rajiv Khare (Alternate) |
| Ministry of Drinking Water and Sanitation, New Delhi | Shri Dinesh Chand Shri Sumit Priyadarshi (Alternate) |
| NSF Safety and Certification India Pvt Ltd, Gurugram |  |  |  | Shri B. B. Singh Shri Nasrin Kashefi (Alternate) |  |  |  |
| Panchayati Raj and Drinking Water Department, Govt. of Odisha, Bhubaneswar | Chief Engineer |
| Plastindia Foundation, Mumbai | Shri Rajiv J. Raval Dr E. Sundaresan (Alternate) |
| Public Health Engineering Department, Government of Rajasthan, Jaipur | Superintending Engineer (D&S) Executive Engineer (D&S) (Alternate) |
| Reliance Industries Limited, Mumbai | Shri S. V. Raju Shri Saurabh Baghal (Alternate) |
| RITES Limited, New Delhi | Shri Pankaj Aggarwal Shri Mukesh Sinha (Alternate) |
| Shaktiman Extrusions Pvt Ltd, Perumbavoor | Shri N. Suresh Shri T. S. Manoj (Alternate) |
| Supreme Industries Limited, Mumbai |  |  |  | Shri G. K. Saxena Shri Anup Mandal (Alternate) |  |  |  |
| Tamil Nadu Water Supply & Drainage Board, Chennai | Engineering Director Joint Chief Engineer (COM) (Alternate) |
| Tata Consulting Engineers Ltd, Mumbai |  |  |  | Representative |  |  |  |
| In Personal Capacity (L-202 Metrozone, Anna Nagar West, Chennai 600040) |  |  |  | Shri G. K. Srinivasan |  |  |  |
| In Personal Capacity (A-59, Sector 35, Noida 201301) |  |  |  | Shri Kanwar A. Singh |  |  |  |
| BIS Directorate General | Shri Arun Kumar S. Scientist ‘E’/Director and Head (Civil Engineering Department) Representing Director General (Ex-officio)] |

Member Secretary

Shrimati Madhurima Madhav

Scientist ‘D’/Joint Director

(Civil Engineering Department), BIS

Composition of Polyolefins and GRP Piping System Subcommittee, CED 50 : 1

| Organization | Representative(s) |
| --- | --- |
| In Personal Capacity (A-59, Sector 35, Noida 201301) | Shri Kanwar A. Singh (Convener) |
| Alom Poly Extrusion Ltd, Kolkata | Shri Arnav Jhunjhunwala Shri Anik Kumar Chowdhury (Alternate) |
| Assam Gas Company Limited, Dibrugarh | Shri Surjaya Tamulik Shri Ahijit Baruah (Alternate) |
| Bhimrajka Impex Limited, Mumbai | Shri V. K. Sharma Shri Vinod Bhimrajka (Alternate) |
| Central Ground Water Board, Faridabad | Shri D. N. Arun Shri K. R. Biswas (Alternate) |
| Central Institute of Plastics Engineering & Technology, Chennai | Dr K. Prakalathan Dr A. K. Mohapatra (Alternate) |
| Central Public Works Department, New Delhi | Shri M. K. Sharma (CSQ) Shri Amar Singh (Alternate) |
| CSIR-National Environmental Engineering Research Institute, Nagpur | Dr (Shrimati) Abha Sargaonkar Dr Ritesh Vijay (Alternate) |
| Chennai Water Supply & Sewerage Board, Chennai | Engineering Director Chief Engineer (O&M) (Alternate) |
| Delhi Jal Board, New Delhi | Shri Y. K. Sharma Shri S. L. Meena (Alternate) |
| Duraline India Pvt Ltd, Mumbai | Shri Rajeev Chaturvedi Shri Sunil Saxena (Alternate) |
| Engineers India Ltd, New Delhi | Shri N. Kaul Shri R. B. Bhutda (Alternate) |
| EPP Composite Pipes, Rajkot | Shri Jayraj Shah Shrimati Seema Vaidya (Alternate) |
| GAIL India Limited, New Delhi | Dr Debasish Roy Shri Manish Khandelwal (Alternate I) Shri Nitin Gupta (Alternate II) |
| Godavari Polymers Pvt Limited, Secunderabad | Shri C. Venkateshwar Rao Shri G. Sridhar Rao (Alternate) |
| Government E-Marketplace, New Delhi | Representative |
| Indraprastha Gas Limited, New Delhi | Representative |
| Industrial Toxicology Research Centre, Lucknow | Dr V. P. Sharma Dr Virendra Misra (Alternate) |
| Jain Irrigation Systems Limited, Jalgaon | Shri M. R. Kharul Shri M. D. Chaudhari (Alternate) |
| Kimplas Piping Systems Ltd, Nashik | Shri Kiran Sarode Shri Santosh Kumar (Alternate) |
| KITEC Industries India Limited, Mumbai | Shri Dalip V. Kolhe Shri Manoranjan G. Choudhary (Alternate) |
| Mahanagar Gas Limited, Mumbai | Shri K. Venugopal Shrimati Neha Kharya (Alternate) |
| Mahanagar Telephone Nigam Limited, New Delhi | Chief Engineer (BW) |
| Maruthi Tubes Pvt Ltd, Secunderabad | Shri Manchaala Raghavendra Shri M. Nagesh Kumar (Alternate) |
| Military Engineer Services, Engineer- in-Chief's Branch, Integrated HQ of MoD (Army), New Delhi | Shri A. K. Dubey Shri R. K. Chauhan (Alternate) |
| National Test House, Kolkata | Shri S. P. Kalia Shri M. M. Pabalkar (Alternate) |
| Ori-Plast Limited, Kolkata | Shri Ashish Agarwal Shri Somnath Mukherjee (Alternate) |
| Public Health & Municipal Engineering Department, Hyderabad | Shri K. Suresh Kumar Shri Ch. Mallikarjunudu (Alternate) |
| Reliance Industries Limited, Mumbai | Shri S. V. Raju Shri Saurabh Baghal (Alternate I) Shri Tushar Dongre (Alternate II) |
| Sangir Plastics Pvt. Ltd., Mumbai | Shri Prashant Trivedi Shri K. V. C. Dora (Alternate) |
| In Personal Capacity (Panchjyot CHS; H-23/01 Sector 29, Vashi, Navi Mumbai 400703) | Shri V. K. Sharma |

Composition of PVC and ABS Piping System Subcommittee, CED 50 : 2

| Organization |  |  | Representative(s) |  |  |
| --- | --- | --- | --- | --- | --- |
| In Personal Capacity (L-202 Metrozone, Anna Nagar West, Chennai 600040) | Shri G. K. Srinivasan (Convener) |
| Ashirvad Pipes Pvt Ltd, Bengaluru | Shri Mohammad Noufal Shri Milind B. Magar (Alternate) |
| Astral Poly Technik Ltd, Ahmedabad | Shri Sandeep Engineer Shri Lalit Trivedi (Alternate) |
| Baerlocher India Additives Pvt Ltd Mumbai | Dr Shreekant Diwan Shri Sachin Bidkar (Alternate) |
| Central Ground Water Board, Faridabad |  |  | Shri D. N. Arun Shri K. R. Biswas (Alternate) |  |  |
| Central Institute of Plastic Engineering & Technology, Chennai | Shri M. Navaneethan |
| Central Public Works Department, New Delhi | Chief Engineer (CSQ) Executive Engineer (S&S) (Alternate) |
| Delhi Jal Board, New Delhi | Shri Y. K. Sharma Shri S. L. Meena (Alternate) |
| Department of Telecommunications Ministry of Communications, Govt of India, New Delhi | Shri V. L. Venkataraman Shri P. Adinarayana (Alternate) |
| Finolex Industries Limited, Pune | Shri Arun Sonawane Shri D. J. Salunke (Alternate) |
| Government E-marketplace, New Delhi | Representative |
| Jain Irrigation Systems Limited, Jalgaon | Shri Narayanaswami Shri M. R. Kharul (Alternate) |
| Kimplas Piping Systems Ltd, Nashik | Representative |
| Mahanagar Telephone Nigam Limited, New Delhi | Superintending Engineer (Civil) Shri M. K. Singhal (Alternate) |
| National Test House, Kolkata | Shri D. Sarkar Dr Nishi Srivastava (Alternate) |
| Optiflux Pipe Industries, Jodhpur | Shri Praveen Parihar Shri Amit Borana (Alternate) |
| Reliance Industries Limited, Mumbai | Shri S. V. Raju Shrimati Aruna Kumari (Alternate I) Shri Jayesh Desai (Alternate II) |
| Rex Polyextrusion Limited, Sangli | Shri Shashank Pargaonkar Shri C. B. Dandekar (Alternate) |
| RITES Limited, New Delhi | Shri Pankaj Aggarwal Shri Mukesh Sinha (Alternate) |
| Rural Water Supply & Sanitation Department, Govt of Orissa, Bhubaneswar | Chief Engineer |
| Supreme Industries Limited, Jalgaon | Shri G. K. Saxena Shri P. L. Bajaj (Alternate) |
| Tamil Nadu Water Supply & Drainage Board, Chennai | Engineering Director Joint Chief Engineer (COM) (Alternate) |
| In Personal Capacity (A-59, Sector 35, Noida 201301) | Shri Kanwar A. Singh |

Composition of the Working Group for UPVC Column Pipes, CED 50/WG2

| Organization | Representative(s) |
| --- | --- |
| Central Institute of Plastic Engineering and Technology, Chennai | Shri M. Navaneethan (Coordinator) |
| Ashirvad Pipes Pvt Ltd, Bengaluru | Shri Mohammad Noufal |
| Astral Polytechnik Ltd, Ahmedabad | Shri Ritesh Patel |
| Duke Pipes Pvt Ltd, Palanpur | Shri Girish A. Patel |
| Finolex Industries Ltd, Pune | Shri D. J. Salunke |
| Jain Irrigation System Ltd, Jalgaon | Shri M. R. Kharul |
| Supreme Industries Ltd, Jalgaon | Shri G. K. Saxena |
| In Personal Capacity (A-59, Sector 35, Noida 201301) | Shri Kanwar A. Singh |