## Slide 2: These standards prescribe quality requirement for various types of valves used:
IS 14845:2000
Resilient seated cast iron air relief valves for water works purposes
1
IS 13095:2020
Butterfly Valves for General Purposes
3
IS 14846:2000
Sluice valve for water works purposes (50 To 1200 mm size)
2
IS 5312(P-1):2004
Swing check type reflux (non-return) valves for water works purposes – Part 1 Single door pattern
4

## Slide 4
17
44
21
17
IS 14845 IS 14846 IS 13095 IS 5312(Part 1)

## Slide 5
I
Types
This Indian Standard covers requirement of single air vaIve (small and large orifice), doubIe air valves (smaII and large orifice with or without integral isolating valve) and kinetic air valves with or without separate isolating sluice valve for use on water mains
Single air valve - Small Orifice type (S1) and Large orifice type (S2)
Double air valve - Standard type with in-built isolating valve (DS 1) or without isolating valves (DS 2)
Kinetic air valve - Kinetic air valve (DK)
The valves shall be designed for maximum permissible gauge working pressure PN 1.0 Mpa and PN 1.6 Mpa
Single air valve (S1) - (Small orifice type) 15, 25, 40 mm
Single air valve (S2) - (Large orifice type) - 25, 40, 50 mm
Double air valve (DS 1, 2) - (All types) - 40, 50, 80,100,150, 200 mm
Kinetic air valve (DK) - 40, 50, 80,100,150, 200 mm
Nominal Pressure & Nominal Sizes

## Slide 6: Scope
Nominal Pressure
This standard covers requirements for non-rising stem type sluice valves from 50 to 1200 mm sizes used for water supply up to 45°C and having double flanged
ends for connections
Nominal Sizes
The sluice valves shall be designed for the following sizes:
50,65,80,100,125,150,200,250,30
0,350,
400,500,600,700,750,800,900,10
00,1100 and 1200mm
Nominal Pressure (PN) | Nominal Sizes
MPa | mm
PN 1.0 | 50 to 1200
PN 1.6 | 50 to 600

## Slide 7: Scope
Size of valve( in mm) | Nominal Pressure(in MPa)
50 to 600 | 1.0 and 1.6

## Slide 8: IS 13095
This standard covers double flanged and wafer type of metal seated, resilient seated cast iron, ductile iron and carbon steel, stainless steel and lined butterfly valves, for general purposes.
Valves covered under this standard are manually, pneumatically, hydraulically or electrically operated.
It covers valves of nominal pressure designations up to and including 4 MPa and Class 300 with ends flanged or wafer type valves with bodies designed to be accommodated between pipe work flanges in accordance with appropriate tables of IS 6418 ‘Cast iron and malleable cast iron flanges for general engineering purposes’, IS 9523 ‘Ductile iron fittings for pressure pipes for water, gas and sewage — Specification’ or
IS 6392 ‘Steel pipe flanges’ in nominal sizes DN 40 to DN 2000.

## Slide 9
 | IS 14845 | IS 14846 | IS 13095 | IS 5312:Part 1
Total Samples Drawn | 0 | 62 | 22 | 38
Total Samples Passing | 0 | 18 | 17 | 24
Total Samples Failures | 0 | 38 | 1 | 12
0
62
22
38
0
18
17
24
0
38
1
12
0
10
20
30
40
50
60
70
Total Samples Drawn Total Samples Passing Total Samples Failures

## Slide 10
 |  | 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  |  |  |  |  |  |  |  |  |  | 7 |  |  |  | 
 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | 
 |  |  |  | 4 |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 
 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  | 
 | 0 0 0 |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  | 0
 | IS 14845 | IS 14846 |  |  |  |  |  |  | IS 13095 |  |  |  |  | IS 5312:Part 1 |  |  |  | 
Total Samples Drawn | 0 | 9 |  |  |  |  |  |  | 3 |  |  |  |  | 7 |  |  |  | 
Total Samples Passing | 0 | 4 |  |  |  |  |  |  | 1 |  |  |  |  | 5 |  |  |  | 
Total Samples Failures | 0 | 2 |  |  |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  | 
10
9
8
7
6
5
4
3
2
1
0
Total Samples Drawn Total Samples Passing Total Samples Failures

## Slide 11
 | IS 14845 | IS 14846 | IS 13095 | IS 5312:Part 1
Total Samples Drawn | 2 | 16 | 8 | 8
Total Samples Passing | 0 | 5 | 6 | 8
Total Samples Failures | 2 | 10 | 0 | 0
2
16
8
8
0
5
6
8
2
10
0
0
0
2
4
6
8
10
12
14
16
18
Total Samples Drawn
Total Samples Passing
Total Samples Failures

## Slide 12
IS 14845 - Sample Failure is attributed to requirement
of dimensions.
IS 13095 - Sample Failure is attributed to requirement
of dimensions.
IS 14846- Sample Failure is attributed to requirement of dimensions (Facing and Seat Rings, Size of Hand
wheel)
IS 5312 : Part 1- Sample failure is attributed to requirement of dimensions (Thickness of flange),
Hydrostatic Seat test

## Slide 13
IS | No. of Visits | Satisfactory | Unsatisfactory
14845 | 45 | 43 | 2
14846 | 116 | 114 | 2
13095 | 55 | 55 | 0
5312 : Part 1 | 53 | 52 | 1
Unsatisfactory visit reported are mostly due to non maintenance of records as per the SIT of the standard |  |  | 

## Slide 14
As per Cl 15 of IS 14845
Each valve body shall be permanently marked with a plate securely fixed to the body with the following information:
Nominal size
Nominal pressure rating
Type of valve
  Single air valve S1, S2, etc
  Double air valve OS 1, DS2, etc
  Kinetic air valve (DK)
Manufacturers name or trade- mark
Sl No. and year of manufacture
As per Cl. 11 of IS 14846
The following information shall be cast on each valve body in raised letters
The manufacturer's name or trade- mark
The nominal pressure of valve (PN 1.0 or PN 1.6)
Size of valve (mm)
Heat number of cast
Year of manufacture
In addition each valve shall bear conspicuously upon it prior to despatch
Serial number in punch, on top of flanges g) Where a valve has been tested for only open end test, it should be marked '0' distinctly and permanently on flanges adjacent to serial number
As per Cl. 21 of IS 13095
Marking shall be cast integral on the body or on a plate securely attached to the body
As per Cl 11 of IS 5312 (Part 1)
Manufacturer’s name or trade-mark
Nominal pressure of valve (PN 1.0 or PN 1.6)
Size of valve, mm
Direction of flow e) Heat No. of cast

## Slide 15
THANK YOU